## requirements
item | text
R1 | They must be able to self-start without any source of off-site electric power and maintain adequate voltage and frequency while energizing isolated transmission facilities and auxiliary loads of other generators.
R2 | Such Test Dispatch Notice shall be marked “Black Start Test Notice.” The Black Start Test shall be performed in accordance with the Ancillary Services Requirements Protocol in the CAISO Tariff.
R3 | The CAISO shall not request a Black Start Test for a hydroelectric Unit during periods of constrained water availability.
R4 | The owner or operator of any Voluntary Black Start unit that desires a Black Start generating unit status with the CAISO Balancing Authority shall: • Demonstrate at least every five years, through simulation or testing, that the unit can perform its intended functions as required by the WECC BCP (if any) and of this testing section. • Submit documentation of the test results and analysis to the CAISO, WECC, or NERC upon any request. • Submit any past reports for Black Start tests with the CAISO and WECC. o Those Participants who do not currently test their Black Start capability, will be required to test their Black Start capability. • Within 24 hours of conducting a Black Start test, all Participants will notify the CAISO RT Dispatcher by phone indicating the success or failure of the test. • Within 14 days of performing a Black Start test, all Participants will file a letter with the CAISO regarding the success or failure of the test.
R5 | Testing records shall include the dates of the tests, the duration of the tests, and an indication of whether the tests met the requirements of this Black Start Testing section.
R6 | The Black Start unit must have the ability to maintain voltage within emergency voltage limits over a range of loading from no external load to full external load in accordance with NERC reliability standards.
R7 | The Black Start unit must be equipped with governors that are capable of operating in an isochronous mode.
R8 | Adequate transmission capacity shall be available to connect the Black Start facility to the source providing station services to other specified generating stations.
R9 | The Black Start unit must be capable of starting and energizing the applicable transmission path without assistance from the electrical system.
R10 | The following start-up/synchronizing time limits shall apply to the Black Start testing units: • Hydroelectric generating units or combustion gas turbines - within 30 minutes of the initiation of the Black Start process, • Industrial gas turbines - within 60 minutes of the initiation of the Black Start process, • Hot, steam-driven turbines, within 2.5 hours of the initiation of the Black Start process. • If the certified Black Start facility is in another reliability coordinator area or is comprised of an unspecified technology then specific start time limits are negotiated.
R11 | All Black Start Generating Units must satisfy technical requirements specified by the CAISO.
R12 | The CAISO shall from time to time undertake performance tests, with or without prior notification.
R13 | The CAISO shall have the sole right to determine when the operation of Black Start Generating Unit is required to respond to conditions on the CAISO Controlled Grid.
R14 | Each of he four points must reside in a different hour of the test.
R15 | If… Then… The a Black Start unit did not successfully pass the CAISO Black Start criteria specified in this procedure, An explanation and a plan to address and correct the deficiency shall be provided to the CAISO by the generator owner/operator.
R16 | The results of the testing and the justification for the periodicity of the testing shall be provided to WECC or NERC on request (within 30 days).
R17 | References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203, Reliability Must Run Unit Commitment and Dispatch CAISO Operating Procedure G-213 Generator Certification Testing CAISO Operating Procedure G-213H Black Start Test Report Form CAISO Operating Procedure G-213I Black Start Process Flowchart NERC Reliability Standard EOP-005 System Restoration Plans EOP-009 Documentation of Blackstart Generating Unit Test Results

## weights
rater | weight
qwen | 0.33333
kimi | 0.33333
glm5 | 0.33333

## round_history
round | n_issue_candidates | n_team_issues_ge_theta | score_converged | issue_converged | max_score_diff | issue_jaccard
0 | 55 | 30 | FALSE | FALSE
1 | 51 | 28 | FALSE | TRUE | 0.66667 | 0.93333

## model_profile
rater | G | B | weight_raw | n_good | n_bad | n_uncertain | n_outliers | weight
qwen | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0.33333
kimi | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.33333
glm5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.33333

## outlier_events
rater | item | dim | dimension | score | confidence | baseline_median | deviation | abs_deviation | delta | rationale | suggestion
qwen | R7 | V | Verifiable | 1 | 0.95 | 3 | -2 | 2 | 2 | No testable criterion is given: no measurable parameter (e.g., frequency deviation ≤ ±0.02 Hz under 0–100% load step), no test condition (e.g., 'during simulated islanded operation with no external grid reference'), and no pass/fail threshold — making verification impossible as written. | Add verifiable acceptance criteria: 'During factory acceptance test (FAT), the governor shall demonstrate frequency regulation within ±0.02 Hz of nominal (50/60 Hz) for three consecutive 20% load steps (0→20→40→60%) in islanded mode, measured using calibrated PMU; deviation exceeding ±0.05 Hz at any 100-ms interval shall constitute failure.'

## outlier_quality
rater | item | dim | abs_deviation | E_evidence | F_falsifiable | R_rewrite_exec | S_specificity | T_taxonomy_fit | D_novelty | Q | hard_fail
qwen | R7 | V | 2 | 2 | 0 | 2 | 0 | 1 | 0 | 0.41667 | FALSE

## outlier_decisions
rater | item | dim | abs_deviation | Q | hard_fail | decision
qwen | R7 | V | 2 | 0.41667 | FALSE | uncertain

## candidates
item | type
R1 | U
R1 | A
R1 | V
R2 | U
R2 | A
R2 | V
R3 | U
R3 | A
R3 | V
R4 | U
R4 | A
R4 | V
R4 | C
R5 | A
R5 | V
R6 | U
R6 | A
R6 | V
R7 | U
R7 | A
R7 | V
R7 | C
R8 | U
R8 | A
R8 | V
R9 | U
R9 | A
R9 | V
R10 | U
R10 | A
R10 | V
R11 | U
R11 | A
R11 | V
R12 | U
R12 | A
R12 | V
R13 | U
R13 | A
R13 | V
R14 | U
R14 | A
R14 | V
R14 | C
R15 | U
R15 | A
R15 | V
R15 | C
R16 | U
R16 | A
R16 | V
R16 | C
R17 | U
R17 | A
R17 | V

## ratings_r0
rater | item | dim | dimension | score | confidence | rationale | suggestion
qwen | R1 | U | Understandable | 2 | 0.9 | 'They must be able to self-start without any source of off-site electric power' lacks subject identification — 'They' is ambiguous (generators? control systems? black-start units?) and violates atomicity; readers cannot determine scope without external context. | Replace with subject-explicit, atomic statement: 'Each designated black-start generator shall initiate its own startup sequence using only on-site energy sources (e.g., batteries, diesel starters, or flywheels), without connection to off-site AC power.'
qwen | R1 | A | Unambiguous | 2 | 0.95 | 'self-start', 'adequate voltage and frequency', and 'isolated transmission facilities' are undefined terms — 'adequate' is subjective, 'isolated transmission facilities' has no boundary specification (voltage level? topology? length?), introducing interpretation variance. | Define all critical terms quantitatively and contextually: 'self-start' → 'achieve rated speed and synchronize within 300 seconds'; 'adequate voltage and frequency' → 'maintain terminal voltage within ±5% of 13.8 kV and system frequency within ±0.05 Hz'; 'isolated transmission facilities' → 'the 138-kV radial feeder segment between Bus A and Substation X, de-energized from the bulk grid and loaded only by the black-start generator and its connected auxiliary loads.'
qwen | R1 | C | Correctness | 3 | 0.8 | The requirement logically aligns with black-start capability standards (e.g., NERC BAL-003), but 'auxiliary loads of other generators' implies cross-generator dependency during islanded operation, which contradicts typical black-start sequencing where only the initiating unit powers its own auxiliaries first; this may reflect a domain misconception. | Revise to reflect correct operational sequence: 'During black-start, the generator shall energize only its own auxiliary loads and the designated isolated transmission facility; it shall not supply auxiliary loads of other generators until those generators have achieved synchronized, stable operation.'
qwen | R1 | V | Verifiable | 1 | 0.98 | No testable thresholds or conditions are provided — e.g., no numeric values for voltage (±% of nominal?), frequency (Hz tolerance?), duration (how long must stability be maintained?), nor defined test configuration (which loads? how many MW? what fault clearance time?). Without these, verification is impossible. | Provide measurable pass/fail criteria: 'Within 60 seconds of synchronization, the generator shall maintain voltage at 13.8 kV ±5% and frequency at 60.00 Hz ±0.05 Hz for ≥300 seconds while supplying a minimum load of 2.5 MW (comprising its own auxiliaries and the isolated 138-kV feeder).'
kimi | R1 | U | Understandable | 3 | 0.75 | 原文使用'They'未指明主体，'adequate voltage and frequency'未给出数值范围，降低可理解性 | 将'They'替换为'每台应急黑启动燃气轮机'，并补充'电压偏差≤±5 %额定值，频率偏差≤±0.5 Hz'
kimi | R1 | A | Unambiguous | 2 | 0.8 | 'self-start''adequate''isolated transmission facilities'等术语缺乏唯一解释，存在多种理解可能 | 定义：'self-start'='在厂用电全失且无任何外部电源情况下，于30 min内完成机组启动并带初始负载'；'isolated transmission facilities'='本厂220 kV升压站及下游空充线路总长≤100 km'
kimi | R1 | C | Correctness | 3 | 0.7 | 未限定启动条件（环境温度、燃料状态）及负载阶跃，无法判断需求是否物理可行 | 补充前提：'在环境温度-10 °C至45 °C、燃料罐液位≥30 %、润滑系统预润滑完成条件下'
kimi | R1 | V | Verifiable | 2 | 0.85 | 'adequate'无量化指标，'maintain'未给出持续时间与容许偏差，测试无法判定通过/失败 | 增加可测试指标：'黑启动后0→25 %额定负载阶跃，电压恢复时间≤5 s，频率瞬变≤±1 Hz，稳态频率偏差≤±0.2 Hz，持续运行≥4 h'
glm5 | R1 | U | Understandable | 3 | 0.9 | 证据片段：'They must be able to...'。代词 'They' 缺乏明确的先行词，读者必须依赖上下文推测主语，且句子结构较长，增加了认知负荷。 | 将代词 'They' 替换为具体的系统组件名称，并将长句拆分为两个独立的原子需求。
glm5 | R1 | A | Unambiguous | 2 | 0.9 | 证据片段：'adequate voltage and frequency'。形容词 'adequate'（充足的）是主观判断，未定义具体的数值范围或标准，导致不同开发者理解不一致。证据片段：'They'。主语指代不明。 | 将 'adequate' 替换为具体的数值范围或引用具体标准，明确主语。
glm5 | R1 | C | Correctness | 3 | 0.6 | 证据片段：'maintain adequate voltage and frequency'。由于缺乏具体的阈值或引用标准，无法判断该需求是否符合电网规范或设备技术规格，正确性无法保证。 | 引用具体的行业标准（如 IEEE 或 IEC 标准）来界定电压和频率的合格范围。
glm5 | R1 | V | Verifiable | 2 | 0.9 | 证据片段：'adequate voltage and frequency'。由于缺乏可量化的数值（如 '220V±5%' 或 '50Hz±0.2Hz'），测试人员无法设计测试用例来客观地判定通过或失败。 | 将 'adequate' 替换为具体的、可测量的数值范围。
qwen | R2 | U | Understandable | 2 | 0.9 | 'Such Test Dispatch Notice' lacks antecedent reference — no prior definition or declaration of 'Test Dispatch Notice' exists in this requirement; readers cannot identify what entity is being marked, violating atomicity and traceability. | Replace with an atomic, self-contained statement defining the artifact: 'The system shall generate a dispatch notice for black start tests.'
qwen | R2 | A | Unambiguous | 2 | 0.95 | 'shall be marked "Black Start Test Notice."' is ambiguous: it does not specify where (e.g., subject line, header, watermark), in what format (plain text, PDF stamp, email metadata), or whether case sensitivity applies — multiple interpretations are possible. | Specify marking location, format, and exact string: 'The dispatch notice PDF shall contain the exact visible text "Black Start Test Notice" centered in the top margin, in 16-point bold Arial font.'
qwen | R2 | C | Correctness | 3 | 0.8 | The reference to 'Ancillary Services Requirements Protocol in the CAISO Tariff' is externally defined and stable; assuming that protocol exists and governs black start tests, correctness is moderately supported, though the requirement does not assert functional alignment with that protocol's test scope or timing. | Keep unchanged — but note: correctness depends on external tariff alignment; no internal inconsistency is evident.
qwen | R2 | V | Verifiable | 1 | 0.98 | No observable, objective pass/fail criterion is provided — e.g., no specification of how compliance is confirmed (e.g., 'system shall generate a PDF with visible header text "Black Start Test Notice" within 5 seconds of dispatch'), making verification impossible without external interpretation. | Replace with a testable condition: 'Upon initiation of a black start test dispatch, the system shall output a file named BS_TEST_NOTICE_YYYYMMDD_HHMMSS.pdf containing the exact string "Black Start Test Notice" as the first non-whitespace line.'
kimi | R2 | U | Understandable | 3 | 0.8 | 原文出现'Such Test Dispatch Notice'，但未在前文定义该术语，读者需回溯才能理解'Such'指代何物，降低可读性 | 将'Such Test Dispatch Notice'替换为显式定义后的名称，如'Black Start Test Dispatch Notice'
kimi | R2 | A | Unambiguous | 2 | 0.9 | 短语'in accordance with the Ancillary Services Requirements Protocol in the CAISO Tariff'未给出具体章节/条款编号，不同人可能定位到不同版本或不同段落，存在解释差异 | 补充精确引用，如'CAISO Tariff第5.2.3节Ancillary Services Requirements Protocol(版本2024-03)'
kimi | R2 | C | Correctness | 4 | 0.7 | 需求仅引用外部协议，未明确若协议更新是否自动适用；一旦CAISO Tariff变更，需求正确性可能失效 | 增加冻结条款，如'以CAISO Tariff 2024-03版为准，若后续版本有冲突，以本需求发布日有效版本优先'
kimi | R2 | V | Verifiable | 2 | 0.9 | 未定义可观察的验证标准，如'marked'是否仅要求页眉出现指定文字、'performed in accordance with'如何判定合规，测试人员无法设计通过/失败准则 | 增加可测标准，如'在PDF页眉居中打印“Black Start Test Notice”，字体Arial 12pt；测试步骤与结果须100%符合CAISO Tariff第5.2.3节表A要求，由独立审计员出具合规报告'
glm5 | R2 | U | Understandable | 3 | 0.9 | 证据片段：“Such Test Dispatch Notice”。使用了指示代词“Such”指代前文内容，导致该条目在孤立阅读时主语不明确，降低了理解的直观性。 | 系统应将测试调度通知标记为“Black Start Test Notice”。
glm5 | R2 | A | Unambiguous | 2 | 0.9 | 证据片段：“shall be marked”。未指明标记的具体位置（如邮件主题、文档页眉、系统字段）和方式，导致实现方式存在歧义。 | 系统应在测试调度通知的【通知类型】字段中显示“Black Start Test Notice”。
glm5 | R2 | C | Correctness | 4 | 0.5 | 证据片段：“Ancillary Services Requirements Protocol in the CAISO Tariff”。假设引用的外部协议存在且正确，该需求在业务逻辑上是成立的，但缺乏对具体规则的直接描述。 | 保持不变。
glm5 | R2 | V | Verifiable | 2 | 0.9 | 证据片段：“performed in accordance with”。属于典型的“按引用包含”，若不获取并解析外部协议的具体内容，无法编写具体的测试用例来验证是否合规。 | 系统应依据《CAISO Tariff》中《Ancillary Services Requirements Protocol》规定的步骤执行黑启动测试，并生成执行日志。
qwen | R3 | U | Understandable | 2 | 0.85 | 'constrained water availability' is a vague, context-dependent qualitative phrase without defined thresholds or measurement method; readers cannot consistently interpret when it applies — evidence: 'periods of constrained water availability'. | Replace with objectively bounded definition using measurable hydrologic parameters.
qwen | R3 | A | Unambiguous | 2 | 0.9 | 'constrained water availability' admits multiple interpretations (e.g., reservoir level < X%, inflow < Y cfs, drought declaration status); absence of objective criteria makes the condition ambiguous — evidence: 'constrained water availability'. | Define 'constrained water availability' as a Boolean condition based on publicly reported, time-stamped data sources.
qwen | R3 | C | Correctness | 3 | 0.75 | The requirement is plausibly correct from operational safety perspective, but lacks traceability to regulatory source (e.g., CAISO Tariff Section 22.3 or FERC Order 881) and does not specify whether this applies to all hydro units or only those designated as black start resources — evidence: 'The CAISO shall not request a Black Start Test for a hydroelectric Unit during periods of constrained water availability'. | Add reference to governing regulation and scope qualifier (e.g., 'for hydroelectric units designated as Black Start Resources per Appendix D of CAISO Tariff').
qwen | R3 | V | Verifiable | 1 | 0.95 | No testable condition is provided: there is no defined metric, threshold, time window, or authoritative data source to determine if 'constrained water availability' holds at a given moment; thus, verification requires subjective judgment — evidence: 'periods of constrained water availability'. | Specify verifiable trigger: e.g., 'when the applicable federal or state drought declaration is active AND the unit's primary reservoir elevation falls below 85% of its normal pool elevation, as reported in real-time by USGS gauge ID XXXX'.
kimi | R3 | U | Understandable | 3 | 0.8 | 原文使用'constrained water availability'这一非专业口语化短语，未给出定义或量化阈值，导致不同角色理解差异，降低可理解性。 | CAISO不得在水库可用水量低于日常最小发电需水量对应水位时，要求水电机组进行黑启动试验。
kimi | R3 | A | Unambiguous | 2 | 0.7 | 'periods of constrained water availability'无明确判定标准，无法确定何时触发禁止，存在多种解释空间，造成歧义。 | CAISO不得在水库水位≤EL. 120 m或收到水务调度'限水运行'指令期间，要求水电机组进行黑启动试验。
kimi | R3 | C | Correctness | 3 | 0.6 | 未说明'constrained'由谁、依据何种规则认定；若未来水资源管理政策变化，需求可能失效，正确性风险高。 | CAISO不得在水库水位≤EL. 120 m或收到水务调度'限水运行'指令期间，要求水电机组进行黑启动试验。
kimi | R3 | V | Verifiable | 2 | 0.7 | 缺少可测指标（如水库水位、入库流量、调度令号等），测试人员无法客观验证'constrained'状态是否成立，从而无法验证需求是否被满足。 | CAISO不得在水库水位≤EL. 120 m或收到水务调度'限水运行'指令期间，要求水电机组进行黑启动试验。
glm5 | R3 | U | Understandable | 3 | 0.8 | 证据片段：'periods of constrained water availability'。虽然句子结构清晰，但关键条件短语缺乏明确的业务定义，不同读者可能对其含义产生不同的理解，影响了整体的可理解性。 | The CAISO shall not request a Black Start Test for a hydroelectric Unit during periods defined as 'constrained water availability' in the Water Management Policy.
glm5 | R3 | A | Unambiguous | 2 | 0.9 | 证据片段：'periods of constrained water availability'。该短语存在显著歧义，未定义'constrained'的具体阈值或判定标准（如水位百分比、流量限制或官方公告），导致无法明确界定触发条件。 | The CAISO shall not request a Black Start Test for a hydroelectric Unit when the reservoir water level is below [Specific Threshold]% or when a drought emergency is declared by [Authority].
glm5 | R3 | C | Correctness | 3 | 0.6 | 证据片段：'The CAISO shall not request...'。需求描述的逻辑关系在语法上是正确的，符合一般业务逻辑，但缺乏具体定义可能导致实际执行偏离真实业务意图，因此给予中等分数。 | 保持不变
glm5 | R3 | V | Verifiable | 2 | 0.9 | 证据片段：'periods of constrained water availability'。由于缺乏可量化的指标（如具体水位数值）或明确的触发事件，测试人员无法客观判定系统是否处于该状态，导致需求不可验证。 | The CAISO shall not request a Black Start Test for a hydroelectric Unit when the reservoir water level is below [Specific Threshold]% or when a drought emergency is declared by [Authority].
qwen | R4 | U | Understandable | 2 | 0.9 | 'Demonstrate at least every five years, through simulation or testing' is vague about scope and method; 'any request' and 'any past reports' lack temporal bounds and scope definition, impairing reader's ability to grasp required actions without external interpretation; the nested bullet 'o Those Participants who do not currently test...' introduces unstructured conditional logic that breaks atomicity and obscures applicability. | Split into atomic, subject-verb-object requirements; replace all conditionals ('if any', 'who do not currently') with explicit scope definitions; eliminate nested bullets and use numbered clauses.
qwen | R4 | A | Unambiguous | 2 | 0.95 | 'Demonstrate... as required by the WECC BCP (if any)' introduces ambiguity: 'if any' makes compliance contingent on unknown existence of a document; 'success or failure of the test' is undefined—no criteria provided for determining either outcome; 'notify... by phone indicating the success or failure' conflates communication modality with functional outcome assessment. | Replace 'if any' with 'as specified in the latest approved edition of the WECC Black Start Capability Procedure (WECC BCP)'; define 'success' as 'full restoration of black start capability per Section 4.2 of WECC BCP-2023' and 'failure' as 'inability to achieve any step in the validated black start sequence within tolerance limits'; replace 'notify... indicating success or failure' with 'transmit a standardized status code (BS-OK or BS-FAIL) via CAISO's designated real-time notification channel'.
qwen | R4 | C | Correctness | 3 | 0.8 | The requirement states Participants 'will be required to test' if they 'do not currently test'—but this is a procedural directive, not a verifiable condition; no normative source confirms this obligation exists in current CAISO/WECC/NERC rules, and 'will be required' is future-tense prescriptive language inconsistent with a requirements specification (which should state what *is* required, not what *will be*). | Replace 'will be required to test their Black Start capability' with 'shall perform an initial black start capability test no later than 180 days after this requirement becomes effective, per Section 5.1 of CAISO Tariff Appendix V'.
qwen | R4 | V | Verifiable | 2 | 0.85 | No objective pass/fail criteria are defined for 'success or failure'; 'within 24 hours' and 'within 14 days' are testable, but 'submit documentation of the test results and analysis to the CAISO, WECC, or NERC upon any request' cannot be verified because 'any request' is non-deterministic and unbounded—there is no trigger condition or observable event that defines when the requirement applies. | Replace 'upon any request' with 'within 5 business days of receipt of a written request from CAISO, WECC, or NERC'; replace 'success or failure of the test' with 'a signed test report containing timestamped evidence of all 7 mandatory sequence steps (per WECC BCP Table 3.1), each annotated with measured voltage/frequency/timing values and deviation tolerances'.
kimi | R4 | U | Understandable | 3 | 0.7 | 原文使用多层嵌套列表与口语化短语'if any'，读者需自行拆解'Demonstrate…that the unit can perform its intended functions'等长句，增加理解成本。 | 将长句拆分为独立原子需求，每条只含一个义务主体、动作、频率、交付物。
kimi | R4 | A | Unambiguous | 3 | 0.7 | 'its intended functions'未指明具体功能清单；'Participants who do not currently test'范围模糊；'success or failure'未定义判定准则，存在多种解释。 | 用唯一术语替换'Participants'，明确'intended functions'对应WECC BCP表X条款Y；定义'success'为≥90%关键参数在表Z限值内。
kimi | R4 | C | Correctness | 3 | 0.7 | 未说明当WECC BCP不存在时是否仍需演示；'any past reports'未限定时间范围，可能要求提交几十年前失效报告，与法规一致性存疑。 | 增加前提条件：仅当WECC BCP适用时执行对应条款；'past reports'限定为最近10年且仍有效。
kimi | R4 | V | Verifiable | 3 | 0.7 | 'Demonstrate through simulation or testing'未规定测试场景、通过阈值及记录格式；'notify…by phone'未要求留痕，无法客观验证是否按时完成。 | 为每条验证活动补充可测标准：测试方案须提前30天提交CAISO备案；电话通知后1小时内发送带时间戳的邮件确认；报告模板采用CAISO-BS-14表格。
glm5 | R4 | U | Understandable | 3 | 0.9 | 需求使用了嵌套的项目符号（'o Those Participants...'）且主语在 'owner or operator' 和 'Participants' 之间切换，导致逻辑结构混乱，难以快速识别责任主体。证据片段：'The owner or operator... shall... o Those Participants who do not currently test...'。 | 将嵌套的项目符号独立为单独的条目，并统一使用 'The Participant' 或 'The owner/operator' 作为主语，保持一致性。
glm5 | R4 | A | Unambiguous | 2 | 0.9 | 存在多处模糊表达：'any past reports' 未定义时间范围；'will be required to test' 缺乏明确的截止时间或触发条件；'intended functions' 缺乏具体定义。证据片段：'Submit any past reports'、'will be required to test'、'perform its intended functions'。 | 将 'any past reports' 修改为具体的时间范围（如 'past 5 years'）；将 'will be required to test' 修改为具体的行动要求（如 'shall conduct a test within X days'）。
glm5 | R4 | C | Correctness | 3 | 0.8 | 原文中 'required by the WECC BCP (if any) and of this testing section' 存在明显的语法错误，介词 'of' 使用不当，影响对需求正确性的理解。证据片段：'required by the WECC BCP (if any) and of this testing section'。 | 修正语法错误，将 'and of this testing section' 改为 'and the requirements of this testing section'。
glm5 | R4 | V | Verifiable | 3 | 0.8 | 虽然部分条款（如 'Within 24 hours'）可验证，但核心性能要求 'perform its intended functions' 缺乏具体的量化标准或验收准则，导致无法客观验证测试是否通过。证据片段：'perform its intended functions'。 | 引用具体的性能标准文档或列出具体的测试通过标准（如启动时间、持续时长等），替换 'perform its intended functions'。
qwen | R5 | U | Understandable | 3 | 0.8 | 'an indication of whether the tests met the requirements of this Black Start Testing section' is abstract and lacks concrete criteria for 'indication' — e.g., pass/fail flag, textual summary, or compliance code; users may interpret it as a checkbox, a narrative comment, or a reference to external documentation, reducing immediate comprehensibility. | Replace with atomic, concrete phrasing specifying data format and intent.
qwen | R5 | A | Unambiguous | 2 | 0.9 | 'an indication of whether the tests met the requirements' is ambiguous: it does not specify *which* requirements (e.g., all? only functional? only safety-critical?) nor define the evaluation basis (e.g., objective pass/fail against acceptance criteria, or subjective engineering judgment). The phrase 'this Black Start Testing section' is circular if the requirement itself resides in that section. | Specify exact compliance scope and unambiguous representation.
qwen | R5 | C | Correctness | 4 | 0.95 | The requirement correctly mandates inclusion of dates, duration, and compliance status — consistent with typical test record expectations for regulatory traceability; no factual or domain-logic error is evident. | 保持不变
qwen | R5 | V | Verifiable | 2 | 0.9 | 'an indication of whether the tests met the requirements' is not testable: there is no defined pass/fail criterion, no specified format (e.g., Boolean field 'compliance_status: true/false'), and no measurable success condition — an auditor cannot objectively verify compliance without knowing what constitutes valid 'indication' or which requirements are being assessed. | Replace with a verifiable, binary, and format-constrained statement.
kimi | R5 | U | Understandable | 4 | 0.8 | 句子结构清晰，关键词'dates、duration、indication'易于理解，但'an indication of whether the tests met the requirements'未说明指示形式，略损可理解性。 | 保持不变
kimi | R5 | A | Unambiguous | 2 | 0.6 | 'an indication of whether the tests met the requirements'未定义指示的格式、取值或判定规则，存在多种解释空间。 | 将'an indication of whether the tests met the requirements'替换为'a Boolean field “testPassed” with value true if all applicable Black Start Test cases defined in Section X.Y pass, otherwise false'。
kimi | R5 | C | Correctness | 3 | 0.7 | 未明确'duration'的计量单位、时区、精度；'dates'是否含起止；'met the requirements'未引用具体条款，无法确认正确性边界。 | 在'duration'后补充'expressed in whole seconds in UTC'；在'dates'后补充'in ISO-8601 format with start and end timestamps'；并引用具体条款编号。
kimi | R5 | V | Verifiable | 2 | 0.6 | 'indication'未规定可测值（如Pass/Fail布尔值、代码、百分比），导致验证时缺乏客观判据。 | 同A维度改写，使验证只需检查布尔字段值。
glm5 | R5 | U | Understandable | 4 | 0.9 | 证据片段：'Testing records shall include the dates of the tests...'。句子语法结构清晰，使用了标准的'shall'语气，易于读者理解大致意图。 | 保持不变
glm5 | R5 | A | Unambiguous | 2 | 0.9 | 证据片段：'dates of the tests' 和 'an indication of whether the tests met the requirements'。'dates'未指明是开始日期、结束日期还是执行日期；'indication'未定义具体格式（如布尔值、枚举字符串或自由文本），导致实现歧义。 | Testing records shall include the start date and time of each test, the duration of each test in minutes, and a test result status of 'Pass' or 'Fail' indicating compliance with the requirements of this Black Start Testing section.
glm5 | R5 | C | Correctness | 4 | 0.6 | 证据片段：'Testing records shall include...'。假设业务背景为标准的测试记录管理，要求记录时间、时长和结果是符合逻辑且正确的，无明显错误。 | 保持不变
glm5 | R5 | V | Verifiable | 2 | 0.9 | 证据片段：'duration of the tests' 和 'indication'。'duration'缺少时间单位（如分钟或小时），无法精确验证数值是否符合预期；'indication'缺少明确的通过/失败判定标准或数据格式，导致验证测试无法编写明确的断言。 | Testing records shall include the start date and time of each test, the duration of each test in minutes, and a test result status of 'Pass' or 'Fail' indicating compliance with the requirements of this Black Start Testing section.
qwen | R6 | U | Understandable | 2 | 0.85 | 'emergency voltage limits' and 'range of loading from no external load to full external load' lack definition; reader cannot determine what constitutes 'emergency' or 'full' without referenced standards or numerical bounds — evidence: 'emergency voltage limits' and 'no external load to full external load'; | Specify numeric voltage bounds (e.g., ±10% of nominal), define 'no external load' as 0 MW ± 0.1 MW and 'full external load' as rated nameplate capacity (X MW), and replace 'emergency voltage limits' with a defined term or direct reference;
qwen | R6 | A | Unambiguous | 2 | 0.9 | 'maintain voltage within emergency voltage limits' is ambiguous because 'emergency voltage limits' is undefined and context-dependent; NERC standards contain multiple voltage tolerance tables (e.g., TOP-004, BAL-003) with differing applicability — evidence: 'in accordance with NERC reliability standards'; | Replace 'emergency voltage limits' with 'voltage limits specified in NERC BAL-003-3 Section 4.2.1 (±10% of nominal voltage at the unit''s high-side bus)';
qwen | R6 | C | Correctness | 3 | 0.75 | The requirement references NERC standards but does not specify which standard(s), revision, or clause; correctness hinges on traceability to a concrete normative source — evidence: 'in accordance with NERC reliability standards'; | Replace 'NERC reliability standards' with 'NERC BAL-003-3 (Effective Date: 2023-07-01) Section 4.2.1 and TOP-004-3 Section 5.3.2';
qwen | R6 | V | Verifiable | 1 | 0.95 | No testable pass/fail criteria: no numeric voltage bounds, no time duration for maintenance, no load step definition (e.g., ramp rate, steady-state dwell), and no measurement conditions (e.g., point of interconnection, instrumentation class) — evidence: 'must have the ability to maintain voltage within emergency voltage limits over a range of loading from no external load to full external load' | Rewrite to: 'The Black Start unit shall maintain voltage at its high-side bus within ±10% of nominal voltage for ≥30 seconds under each of the following steady-state loading conditions: (a) 0.0 MW ± 0.1 MW, (b) 50% of rated nameplate capacity ± 1%, and (c) 100% of rated nameplate capacity ± 1%, measured using Class 0.2 instrumentation per IEEE C57.13.'
kimi | R6 | U | Understandable | 3 | 0.8 | 短语'emergency voltage limits'与'in accordance with NERC reliability standards'未给出具体数值或标准条款，读者需额外查阅外部文档才能理解完整要求 | The Black Start unit shall maintain its output voltage between 0.95 pu and 1.05 pu while supplying active power from 0 % to 100 % of its nameplate rating, as defined in NERC PRC-024-2 clause 4.3.
kimi | R6 | A | Unambiguous | 2 | 0.9 | 'emergency voltage limits'与'full external load'未定义具体数值或百分比，存在多种解释空间；'NERC reliability standards'未指明具体条款 | The Black Start unit shall maintain its output voltage between 0.95 pu and 1.05 pu while supplying active power from 0 % to 100 % of its nameplate rating, as defined in NERC PRC-024-2 clause 4.3.
kimi | R6 | C | Correctness | 3 | 0.7 | 需求未说明'Black Start unit'指柴油发电机、储能还是其他类型，无法判断其技术可行性是否满足NERC标准 | The Black Start diesel generator shall maintain its output voltage between 0.95 pu and 1.05 pu while supplying active power from 0 % to 100 % of its nameplate rating, as defined in NERC PRC-024-2 clause 4.3.
kimi | R6 | V | Verifiable | 2 | 0.9 | 未给出可测量的电压带、负载步长、测试持续时间和允差，测试人员无法设计验证用例 | During factory acceptance test, the Black Start unit shall be stepped from 0 % to 25 %, 50 %, 75 % and 100 % of nameplate active power; voltage shall remain within 0.95–1.05 pu for ≥5 min at each step with maximum 2 % overshoot and recovery time ≤2 s.
glm5 | R6 | U | Understandable | 4 | 0.9 | 句子结构清晰，使用了'The Black Start unit'、'maintain voltage'等标准术语，语法通顺，易于阅读理解。 | 保持不变
glm5 | R6 | A | Unambiguous | 2 | 0.9 | 证据片段'in accordance with NERC reliability standards'存在歧义，NERC标准众多，未指明具体标准编号及版本；证据片段'emergency voltage limits'未定义具体数值范围，导致不同读者可能产生不同理解。 | The Black Start unit shall maintain voltage within the High and Low Emergency Voltage limits defined in Table X (e.g., 0.95 p.u. to 1.05 p.u.) over a range of loading from no external load to full external load, in accordance with NERC PRC-024-2.
glm5 | R6 | C | Correctness | 3 | 0.8 | 需求描述的功能逻辑在领域内通常是正确的，但由于引用了笼统的'NERC reliability standards'，无法确认其是否精确引用了适用的特定技术条款，存在引用错误的风险。 | The Black Start unit shall maintain voltage within [Specific Voltage Range] over a range of loading from no external load to full external load, complying with the specific requirements of NERC [Standard ID].
glm5 | R6 | V | Verifiable | 2 | 1 | 证据片段'emergency voltage limits'缺乏具体的数值定义，且'range of loading'未指定测试的具体负载点，导致测试人员无法设计明确的通过/失败判定标准。 | The Black Start unit shall maintain terminal voltage between [Min Voltage] and [Max Voltage] when the external load is varied from 0% to 100% of rated capacity in steps of [Step Value], as verified against the criteria in NERC [Standard ID].
qwen | R7 | U | Understandable | 2 | 0.85 | 'capable of operating in an isochronous mode' is vague and lacks context for non-expert readers; no definition of 'isochronous mode' is provided, nor whether it applies to all load conditions or only specific ones — this reduces Understandability. | Replace with atomic, self-contained definition: 'The Black Start unit's governor shall maintain system frequency within ±0.02 Hz of 50 Hz (or 60 Hz, per site specification) when operating in islanded mode with no external grid reference and under load steps from 0% to 100% rated output.'
qwen | R7 | A | Unambiguous | 2 | 0.9 | 'capable of operating' introduces ambiguity: does it mean the governor must support isochronous mode by design, or must it be configured and verified to operate in that mode during black start? The phrase fails to specify activation condition, scope (e.g., frequency range, response time), or functional boundary — violating Unambiguity. | Specify mandatory configuration and activation: 'The governor shall be pre-configured and locked in isochronous control mode prior to black start initiation, and shall remain in that mode throughout the black start sequence until grid synchronization.'
qwen | R7 | C | Correctness | 3 | 0.75 | The requirement aligns with standard black start practices where isochronous control is typical for initial grid restoration; no evidence contradicts technical correctness, though it omits dependency on unit type (e.g., hydro vs. gas turbine) — hence moderate score. | Keep unchanged — but add traceability note in rationale: 'This reflects IEEE 1547-2018 Annex D and NERC PRC-006-2 requirements for islanded frequency regulation during restoration.'
qwen | R7 | V | Verifiable | 1 | 0.95 | No testable criterion is given: no measurable parameter (e.g., frequency deviation ≤ ±0.02 Hz under 0–100% load step), no test condition (e.g., 'during simulated islanded operation with no external grid reference'), and no pass/fail threshold — making verification impossible as written. | Add verifiable acceptance criteria: 'During factory acceptance test (FAT), the governor shall demonstrate frequency regulation within ±0.02 Hz of nominal (50/60 Hz) for three consecutive 20% load steps (0→20→40→60%) in islanded mode, measured using calibrated PMU; deviation exceeding ±0.05 Hz at any 100-ms interval shall constitute failure.'
kimi | R7 | U | Understandable | 3 | 0.7 | 原文使用'Black Start unit'与'governors'等术语，但未给出定义或范围，读者需额外背景知识才能理解 | 保持不变
kimi | R7 | A | Unambiguous | 3 | 0.7 | 'Black Start unit'未指明是单台机组还是一类机组；'equipped with governors'未说明是物理安装还是功能具备；'capable of operating'未给出判定条件 | 保持不变
kimi | R7 | C | Correctness | 3 | 0.7 | 未引用任何标准或法规来界定'isochronous mode'的技术要求，无法判断需求是否完整正确 | 保持不变
kimi | R7 | V | Verifiable | 3 | 0.7 | 未给出验证场景、验收准则或量化指标，测试人员无法设计可重复的验证步骤 | 保持不变
glm5 | R7 | U | Understandable | 4 | 0.9 | 文本使用了标准的工程术语，语法结构清晰，易于理解。证据片段：'Black Start unit'、'governors'、'isochronous mode'。 | 保持不变。
glm5 | R7 | A | Unambiguous | 4 | 0.8 | 术语 'isochronous mode' 在控制工程领域有标准定义（恒定频率控制），'capable of' 指明了能力要求，语义相对明确。证据片段：'isochronous mode'。 | 保持不变。
glm5 | R7 | C | Correctness | 3 | 0.9 | 使用了 'must' 而非需求工程标准关键词 'shall'。根据 ISO/IEC/IEEE 29148 标准，'shall' 应用于定义强制性需求，'must' 通常用于描述自然规律或不可违背的约束，此处用法不规范。证据片段：'must be equipped'。 | The Black Start unit shall be equipped with governors that are capable of operating in an isochronous mode.
glm5 | R7 | V | Verifiable | 3 | 0.8 | 需求缺乏具体的验收标准。'capable of operating' 仅描述了能力，未定义在该模式下运行的性能指标（如频率稳定性、负载调整率），导致验证测试缺乏明确的通过准则。证据片段：'capable of operating in an isochronous mode'。 | The Black Start unit shall be equipped with governors capable of isochronous operation, maintaining a steady-state frequency deviation within ±[X] Hz under [Y]% load steps.
qwen | R8 | U | Understandable | 2 | 0.85 | 'Adequate transmission capacity' is vague and lacks quantifiable criteria; users cannot determine what 'adequate' means without context or thresholds — evidence: 'Adequate transmission capacity shall be available'; | Specify minimum rated capacity (in MVA) and voltage level for the transmission path between the Black Start facility and its designated station service source;
qwen | R8 | A | Unambiguous | 2 | 0.9 | 'Adequate' is inherently subjective and context-dependent; 'the source providing station services to other specified generating stations' is ambiguous about which source (e.g., specific substation, voltage level, or grid node) — evidence: 'the source providing station services to other specified generating stations'; | Replace 'Adequate transmission capacity' with 'Transmission capacity rated ≥ 25 MVA at 34.5 kV' and identify the station service source as 'Substation SS-BS01, Bus B2, per Appendix A';
qwen | R8 | C | Correctness | 3 | 0.75 | The requirement does not contradict known black start standards (e.g., NERC PRC-002), but omits critical technical constraints like voltage level, fault current contribution, or thermal limits — evidence: no mention of voltage class, duration, or system interface point; | Keep unchanged pending system architecture review; however, add dependency on R3 (Grid Interface Specification) to ensure consistency;
qwen | R8 | V | Verifiable | 1 | 0.95 | No testable criterion is provided: no measurable quantity (e.g., MW, MVA, kV), no acceptance threshold, no defined test condition or method — evidence: 'shall be available' is non-falsifiable and unverifiable without metrics or conditions; | Rewrite to require demonstrable capacity via steady-state load flow analysis showing ≤ 5% voltage drop and ≥ 1.2 pu short-circuit ratio at the interconnection point under N-1 contingency.
kimi | R8 | U | Understandable | 3 | 0.8 | 原文使用'Adequate transmission capacity'与'station services'等术语，但未给出容量阈值或服务范围，导致不同角色理解差异，降低可理解性。 | 保持术语但补充定义：'Black Start facility'指具备黑启动能力的XX MW燃机站；'station services'指厂用电负荷。
kimi | R8 | A | Unambiguous | 2 | 0.8 | 'Adequate'与'other specified generating stations'均未量化或枚举，无法确定'足够'标准及'指定'清单，存在显著歧义。 | 将'Adequate'改为'≥150 MVA连续输送能力'；将'other specified generating stations'枚举为'A站、B站、C站'。
kimi | R8 | C | Correctness | 3 | 0.7 | 需求未说明'transmission capacity'所属电压等级、持续时间或N-1准则，无法判断其正确性与完整性。 | 补充技术条件：在最高环境温度40 ℃、单回线路N-1停运情况下，输送能力仍满足≥150 MVA。
kimi | R8 | V | Verifiable | 2 | 0.8 | 无容量数值、测试条件及观测点，验收时无法设计测试用例验证'capacity shall be available'。 | 增加验收条款：在Black Start试验期间，测量线路首末端功率，15分钟平均值≥150 MVA，持续2小时无设备过载报警。
glm5 | R8 | U | Understandable | 3 | 0.8 | 证据片段：'connect the Black Start facility to the source providing station services to other specified generating stations'。句子嵌套层级过深，需多次解析'source providing...'的修饰关系才能理解连接对象，增加了认知负荷。 | 将长句拆分为多个短句，明确连接路径。例如：'Transmission capacity shall connect the Black Start facility to the station service source. This source shall supply services to the generating stations listed in [Reference ID].'
glm5 | R8 | A | Unambiguous | 2 | 0.9 | 证据片段：'Adequate transmission capacity'、'specified generating stations'。'Adequate'是主观形容词，缺乏量化标准；'specified'指代不明，未说明是在何处指定的，导致需求存在多种解释。 | 将模糊词汇替换为具体参数或引用。例如：'The transmission capacity shall be at least [X] MW.'
glm5 | R8 | C | Correctness | 3 | 0.6 | 证据片段：'source providing station services'。虽然逻辑上看似合理，但由于缺乏上下文引用，无法确认'specified generating stations'的列表是否存在于其他文档中，影响了需求的完整性和正确性。 | 补充缺失的引用或定义。例如：'...to generating stations specified in [Document ID, Section X].'
glm5 | R8 | V | Verifiable | 2 | 0.9 | 证据片段：'Adequate transmission capacity'、'shall be available'。由于没有定义'Adequate'的具体数值阈值（如MW数）或标准，测试人员无法客观判断容量是否满足要求；'available'也未定义可用性状态的具体条件。 | 增加可量化的验收标准。例如：'The transmission capacity between [Point A] and [Point B] shall be verified to be greater than or equal to [X] MW under [Condition Y].'
qwen | R9 | U | Understandable | 2 | 0.85 | 'applicable transmission path' is vague and lacks definition; readers cannot determine which path(s) apply without external context or system scope — evidence: 'applicable transmission path'; this violates understandability because stakeholders (e.g., testers, operators) cannot independently interpret the scope. | Replace 'applicable transmission path' with a precisely scoped, traceable identifier such as 'the 230 kV transmission path between Substation Alpha and Bus Gamma, as defined in System Architecture Document v2.1, Section 4.3'.
qwen | R9 | A | Unambiguous | 2 | 0.9 | 'without assistance from the electrical system' is ambiguous: does it exclude only grid-connected power sources, or also auxiliary batteries, diesel generators, or DC control power? Evidence: 'without assistance from the electrical system' — the term 'electrical system' is undefined and overlaps with multiple subsystems, enabling conflicting interpretations. | Replace 'without assistance from the electrical system' with 'using only on-site, non-grid-dependent energy sources (i.e., dedicated black start diesel generator and/or battery bank supplying control and prime mover power), and with zero reliance on AC voltage or current sourced from the bulk electric system'.
qwen | R9 | C | Correctness | 3 | 0.75 | The requirement is plausibly correct for black start functionality, and no internal contradiction or factual error is evident in the statement; evidence: 'The Black Start unit must be capable of starting and energizing...' aligns with IEEE 1344 and NERC TOP-002 standards for black start capability. | Keep unchanged.
qwen | R9 | V | Verifiable | 1 | 0.95 | No testable success criterion is provided — e.g., no defined time limit, voltage/frequency tolerance, path topology, or measurable energization state. Evidence: 'must be capable of starting and energizing' is purely capability-oriented and lacks observable, objective pass/fail conditions. | Replace entire clause with: 'Within 120 seconds of initiation, the Black Start unit shall establish and maintain ≥ 0.95 p.u. voltage and 59.95–60.05 Hz frequency at the receiving end of the 230 kV transmission path between Substation Alpha and Bus Gamma, measured per IEEE 1159 Class A power quality monitoring.'
kimi | R9 | U | Understandable | 3 | 0.8 | 原文'applicable transmission path'未指明具体路径，读者需额外上下文才能理解范围，降低直观性。 | 将'applicable transmission path'替换为具体线路名称或电压等级范围。
kimi | R9 | A | Unambiguous | 2 | 0.9 | 'applicable'与'without assistance'均未定义判定准则，可因不同解读产生歧义。 | 删除'applicable'并给出唯一路径标识；将'without assistance'限定为'零外部电源输入'。
kimi | R9 | C | Correctness | 3 | 0.7 | 未给出'starting'与'energizing'的电压/时间阈值，无法判断需求是否技术上可行或完整。 | 补充'在30分钟内将线路电压升至≥230 kV并保持≥15分钟'等量化指标。
kimi | R9 | V | Verifiable | 2 | 0.9 | 缺乏可观测指标（如电压等级、建立时间、允许的最大外部能量），测试人员无法设计验证步骤。 | 增加可测条件：'在试验中记录黑启动机组输出功率、线路电压曲线，且全程无外部电源输入'。
glm5 | R9 | U | Understandable | 4 | 0.9 | 证据片段：'Black Start unit'、'transmission path'。使用了标准的电力工程术语，句子结构清晰，但对于非领域专家可能存在理解门槛，整体可读性良好。 | 保持不变。
glm5 | R9 | A | Unambiguous | 2 | 0.9 | 证据片段：'applicable transmission path'、'without assistance'。'applicable'未定义具体指哪条路径，导致范围模糊；'without assistance'未界定'协助'的具体形式（如功率辅助、控制信号辅助等），存在多种解释。 | The Black Start unit shall start and energize the transmission path defined in [System_Configuration_Data] while isolated from the external electrical grid.
glm5 | R9 | C | Correctness | 4 | 0.6 | 证据片段：'starting and energizing... without assistance from the electrical system'。该描述符合'黑启动'的标准定义，即在不依赖外部电网支持的情况下恢复供电，逻辑上正确。 | 保持不变。
glm5 | R9 | V | Verifiable | 2 | 0.9 | 证据片段：'capable of'、'without assistance'。'capable of'描述的是一种潜能而非具体动作，难以直接测试；'without assistance'缺乏量化标准，无法设计明确的通过/失败准则。 | The Black Start unit shall start and energize the designated transmission path within [Time_Limit] seconds without drawing power from the external electrical grid.
qwen | R10 | U | Understandable | 2 | 0.9 | 'Hot, steam-driven turbines, within 2.5 hours' lacks subject-verb agreement and omits 'shall start' or equivalent verb; the bullet list mixes noun phrases ('Hydroelectric generating units...') with incomplete clauses, impairing readability and comprehension for non-native speakers and reviewers. The phrase 'If the certified Black Start facility is in another reliability coordinator area or is comprised of an unspecified technology then specific start time limits are negotiated' uses passive voice and vague terms ('negotiated', 'unspecified technology') without defining responsible party or timeframe, reducing understandability. | The Black Start testing units shall achieve full synchronization with the grid within the following maximum elapsed times after the official initiation signal: (a) hydroelectric generating units and combustion gas turbines: 30 minutes; (b) industrial gas turbines: 60 minutes; (c) steam-driven turbine units operating in hot standby mode: 2.5 hours; (d) all other certified Black Start facilities: a time limit mutually agreed upon in writing by the Reliability Coordinator and the facility owner prior to testing.
qwen | R10 | A | Unambiguous | 2 | 0.95 | 'Hot, steam-driven turbines' is ambiguous: does it mean 'turbines that are hot' (thermal state) or 'turbines driven by hot steam' (design type)? Also, 'unspecified technology' is inherently ambiguous—no criteria define what constitutes 'unspecified'; 'reliability coordinator area' is undefined in this requirement and may vary across jurisdictions, introducing interpretation variance. | Keep unchanged
qwen | R10 | C | Correctness | 3 | 0.8 | The requirement appears technically plausible for black start timing categories, and no internal contradiction or factual error is evident from domain knowledge (e.g., steam units typically require longer warm-up); however, 'Hot, steam-driven turbines' may incorrectly imply operational readiness state rather than unit type—potentially conflating condition with classification—so correctness is moderate pending clarification. | Replace 'Hot, steam-driven turbines' with 'steam-driven turbine units operating in hot standby mode' to align with NERC PRC-005-6 terminology and avoid conflation of thermal state with unit category.
qwen | R10 | V | Verifiable | 1 | 0.95 | No test procedure, measurement method, or pass/fail criterion is specified: e.g., 'within 30 minutes' lacks definition of 'initiation' (clock start trigger), 'start-up/synchronizing time' is not defined (is it first rotation? grid synchronization? stable power delivery?), and 'negotiated' time limits are untestable by objective means. Absence of measurable observables makes verification impossible per ISO/IEC/IEEE 29148. | For each unit type, the elapsed time shall be measured from the timestamp of the official Black Start initiation command (issued by the Reliability Coordinator) to the timestamp of verified, stable grid synchronization (defined as sustained 60 Hz frequency ±0.05 Hz and voltage within ±5% of nominal for ≥30 seconds), recorded by a calibrated, tamper-evident data acquisition system.
kimi | R10 | U | Understandable | 3 | 0.7 | 原文使用'start-up/synchronizing time limits'并列，未明确是'启动'还是'并网'，且'initiation of the Black Start process'未定义触发事件，降低可读性。 | 将'start-up/synchronizing time limits'拆分为两条独立需求：启动完成时间、并网完成时间，并定义'Black Start process initiation'为'调度员下达黑启动指令瞬间'。
kimi | R10 | A | Unambiguous | 3 | 0.7 | 'unspecified technology then specific start time limits are negotiated'未指明由谁、何时、如何谈判，存在多方解释空间。 | 删除'negotiated'，改为'由系统调度机构与机组业主在测试计划书中书面约定启动完成时间，且该时间≤4小时'。
kimi | R10 | C | Correctness | 3 | 0.7 | 未给出'Hot, steam-driven turbines'的温度阈值，也未说明'certified Black Start facility'的认证标准，无法判断正确性。 | 补充'Hot'定义：'主蒸汽压力≥8 MPa且温度≥500 °C'；引用认证标准如NERC BAL-005。
kimi | R10 | V | Verifiable | 3 | 0.7 | 'negotiated'结果无定量指标，测试人员无法设计通过/失败准则，导致不可验证。 | 所有机组类型均给出单一数值时限，删除谈判条款，使测试用例可直接比对实测分钟数。
glm5 | R10 | U | Understandable | 4 | 0.9 | 证据片段：'start-up/synchronizing time limits'。使用斜杠'/'连接两个术语，导致语义不清，读者难以判断是指'启动时间'与'同步时间'两个独立指标，还是指'从启动到同步的时间'。 | 将'start-up/synchronizing time limits'修改为'start-up to synchronizing time limits'，明确时间起止点。
glm5 | R10 | A | Unambiguous | 2 | 0.9 | 证据片段：'Hot, steam-driven turbines' 和 'specific start time limits are negotiated'。'Hot'缺乏明确定义（如具体的温度阈值或停机时长），导致状态判断歧义；'negotiated'描述的是一个过程而非确定的结果，导致需求执行标准模糊。 | 定义'Hot'的具体参数（例如：停机时间小于X小时或金属温度高于Y度）；将'negotiated'改为要求明确记录数值的强制性条款。
glm5 | R10 | C | Correctness | 3 | 0.6 | 证据片段：'specific start time limits are negotiated'。从需求工程角度看，需求应规定明确的约束条件，而非描述'协商'这一行为过程，这可能导致需求交付物缺失具体的验收标准，影响需求的正确性。 | 将'negotiated'替换为具体的文档引用或默认值设定，确保需求包含确定的约束。
glm5 | R10 | V | Verifiable | 2 | 0.9 | 证据片段：'Hot, steam-driven turbines' 和 'negotiated'。由于'Hot'状态未量化，测试人员无法客观判定设备是否处于该状态；'negotiated'未指定协商结果的存储位置或生效条件，导致无法验证最终的时间限制是否符合要求。 | 补充'Hot'的量化定义，并要求'negotiated'的结果必须记录在指定文档中以便验证。
qwen | R11 | U | Understandable | 2 | 0.9 | 'All Black Start Generating Units' lacks definition — 'Black Start Generating Units' is undefined and context-dependent; readers cannot determine scope without external domain knowledge. Evidence: 'All Black Start Generating Units'. | Define 'Black Start Generating Unit' as a generating unit certified by CAISO for black start service per CAISO Tariff Section 27.3(a)(1), capable of initiating energization without off-site power.
qwen | R11 | A | Unambiguous | 2 | 0.95 | 'must satisfy technical requirements specified by the CAISO' is ambiguous because 'technical requirements' is a non-specific reference to an external, unversioned, and unbounded document set; no identifier, version, or clause is provided. Evidence: 'technical requirements specified by the CAISO'. | Replace with: 'Each Black Start Generating Unit shall comply with all mandatory technical criteria in CAISO Tariff Appendix D, Revision 4.2 (effective 2023-09-15), Sections D.1 through D.5.'
qwen | R11 | C | Correctness | 3 | 0.8 | The requirement does not contradict known CAISO practice (CAISO does regulate black start units), so correctness is plausible; however, absence of normative source citation reduces confidence. Evidence: 'must satisfy technical requirements specified by the CAISO'. | Keep unchanged — but add normative reference: 'as defined in CAISO Tariff Section 27.3'.
qwen | R11 | V | Verifiable | 1 | 0.95 | No testable criterion is stated — e.g., no measurable parameter, pass/fail condition, or verification method (e.g., document review, functional test, certification audit). Evidence: 'must satisfy technical requirements' — satisfaction is undefined and unobservable. | Each Black Start Generating Unit shall demonstrate compliance via submission of a valid CAISO Black Start Certification Letter issued within the prior 12 months, verified by the System Operator during unit registration.
kimi | R11 | U | Understandable | 3 | 0.8 | 原文'All Black Start Generating Units must satisfy technical requirements specified by the CAISO'中未定义'Black Start Generating Unit'，读者需额外背景知识才能理解。 | 将'Black Start Generating Unit'替换为'能够在全站失电后无需外部电源、于30分钟内带动厂用负荷并具备向电网送电能力的机组'。
kimi | R11 | A | Unambiguous | 2 | 0.9 | 'technical requirements specified by the CAISO'未指明具体文档或版本，存在多种解释空间。 | 将'technical requirements specified by the CAISO'替换为'CAISO Technical Bulletin 2023-01《Black Start Unit Certification Criteria》第4-7节'。
kimi | R11 | C | Correctness | 2 | 0.8 | 未给出CAISO技术要求的有效版本或发布日期，可能随时间变化导致需求失效。 | 在需求中引用'CAISO Technical Bulletin 2023-01（生效日期2023-06-01）'并注明版本锁定策略。
kimi | R11 | V | Verifiable | 1 | 0.95 | 无量化指标或测试步骤，无法设计用例验证是否'满足'要求。 | 增加可测试条款：'机组应在型式试验中于30分钟内完成黑启动并建立≥5%额定电压，试验报告须由CAISO认可的第三方出具'。
glm5 | R11 | U | Understandable | 4 | 0.9 | 证据片段：'All Black Start Generating Units must satisfy...'。句子语法结构清晰，使用了标准的行业术语，对于领域专家而言易于理解。 | 保持不变。
glm5 | R11 | A | Unambiguous | 2 | 0.9 | 证据片段：'technical requirements specified by the CAISO'。'technical requirements' 指代过于宽泛，未指明具体文档、版本号或条款号，导致需求范围界定模糊，存在歧义。 | All Black Start Generating Units must satisfy the technical requirements specified in 'CAISO Tariff Section [X]' or 'BPM for Managing Full Frequency Response', Version [Y].
glm5 | R11 | C | Correctness | 3 | 0.6 | 证据片段：'specified by the CAISO'。在没有外部领域知识验证 CAISO 是否确实规定了这些要求的情况下，无法完全确认其正确性，但逻辑上符合业务语境。 | 保持不变。
glm5 | R11 | V | Verifiable | 2 | 0.9 | 证据片段：'satisfy technical requirements'。由于缺乏具体的量化指标或明确的引用文档，测试人员无法构建具体的测试用例来判断是否满足要求。 | All Black Start Generating Units must satisfy the technical requirements specified in 'CAISO Tariff Section [X]' or 'BPM for Managing Full Frequency Response', Version [Y].
qwen | R12 | U | Understandable | 2 | 0.9 | 'from time to time' is vague temporal phrasing lacking defined frequency or trigger condition; users cannot reliably interpret how often tests occur — evidence: 'from time to time'. | Replace with a bounded frequency or event-driven trigger (e.g., 'at least quarterly' or 'within 72 hours of a grid disturbance exceeding 500 MW imbalance').
qwen | R12 | A | Unambiguous | 2 | 0.95 | 'with or without prior notification' introduces ambiguity about notification policy: it neither specifies when notification is required nor defines acceptable delay windows or exceptions — evidence: 'with or without prior notification'. | Specify explicit conditions for notification: e.g., 'with at least 48 hours written notice for scheduled tests; unscheduled tests permitted only during declared grid emergencies'.
qwen | R12 | C | Correctness | 3 | 0.8 | The requirement does not contradict domain knowledge (CAISO does conduct performance tests), and no factual inaccuracy is evident; however, absence of scope or purpose limits contextual correctness — evidence: 'undertake performance tests' lacks test type, scope, or objective. | Keep unchanged but recommend traceability to test standards (e.g., NERC PRC-005); minimal suggestion: 'Keep unchanged'.
qwen | R12 | V | Verifiable | 1 | 0.95 | No measurable criterion, pass/fail condition, timing constraint, or observable outcome is specified; 'undertake' is an activity verb, not a verifiable result — evidence: 'shall ... undertake performance tests'. | Replace with a test execution and reporting obligation: e.g., 'shall execute and document results of at least one end-to-end contingency analysis validation test per calendar quarter, with all test inputs, configurations, and pass/fail determinations archived for audit'.
kimi | R12 | U | Understandable | 3 | 0.8 | 短语'from time to time'未给出任何周期或触发条件，读者无法判断测试频率，降低可理解性。 | CAISO shall execute performance tests at least once per calendar quarter.
kimi | R12 | A | Unambiguous | 2 | 0.9 | 'with or without prior notification'在同一句话内并列两种完全相反的情形，未说明何时需提前通知、何时可免，存在明显歧义。 | CAISO may conduct performance tests either (a) with no less than 10 business days prior written notice, or (b) without notice when required for emergency reliability assessment.
kimi | R12 | C | Correctness | 3 | 0.7 | 需求仅声明CAISO'shall undertake'，未定义测试通过/失败标准、范围或最低覆盖率，无法判断 correctness 的达成条件。 | Each performance test shall cover no less than 80 % of critical-path transactions and achieve ≤ 2 second 95th-percentile response time to be deemed successful.
kimi | R12 | V | Verifiable | 1 | 0.95 | 无量化指标（频率、通知时限、测试类型、通过准则），测试人员无法设计验证步骤，基本不可验证。 | Compliance is verified by (i) quarterly test execution records, (ii) dated notification emails, and (iii) test reports showing ≥ 80 % coverage and ≤ 2 s 95th-percentile response time.
glm5 | R12 | U | Understandable | 4 | 0.9 | 证据片段'from time to time'虽然语法通顺且易于阅读，但语义较为模糊，读者难以把握具体的执行频率，影响了理解的精确性。 | 保持不变。
glm5 | R12 | A | Unambiguous | 2 | 0.95 | 证据片段'from time to time'属于模糊量词，缺乏明确的定义或量化标准，导致不同读者对测试频率产生不同的解释，存在明显歧义。 | The CAISO shall undertake performance tests at least once per calendar year, with or without prior notification.
glm5 | R12 | C | Correctness | 3 | 0.6 | 需求描述了主体行为，但在缺乏业务背景的情况下，无法确认模糊的频率描述是否准确反映了业务意图或合规要求，存在正确性风险。 | The CAISO shall undertake performance tests at least once per calendar year, with or without prior notification.
glm5 | R12 | V | Verifiable | 2 | 0.95 | 证据片段'from time to time'无法被客观度量或计数，测试人员无法设计明确的通过/失败标准来验证该需求是否已被满足。 | The CAISO shall undertake performance tests at least once per calendar year, with or without prior notification.
qwen | R13 | U | Understandable | 2 | 0.85 | The phrase 'respond to conditions on the CAISO Controlled Grid' is overly vague and lacks concrete operational context; users cannot reliably infer what grid conditions (e.g., frequency deviation >0.05 Hz for >30 s, loss of ≥200 MW generation) trigger black start activation — this impairs understandability. | Replace with atomic, context-grounded language specifying triggering grid events.
qwen | R13 | A | Unambiguous | 2 | 0.9 | 'Sole right to determine when... is required' introduces ambiguity: it conflates authority (who decides) with objective criteria (what constitutes a requirement). The term 'required' is normative and undefined — is it required by reliability standards? By NERC TOP-005? By CAISO tariff? Absence of binding reference creates interpretive divergence. | Explicitly decouple decision authority from objective activation criteria using normative references.
qwen | R13 | C | Correctness | 3 | 0.75 | The statement is plausibly correct as a delegation of operational authority, and aligns with CAISO's FERC jurisdictional role; however, it omits explicit linkage to governing documents (e.g., 'per CAISO Tariff Section 22.3 or NERC Reliability Standard BAL-003-1'), reducing traceable correctness. | Anchor the authority to a cited, versioned regulatory or procedural source.
qwen | R13 | V | Verifiable | 1 | 0.95 | No testable condition or observable outcome is specified — there is no measurable signal (e.g., 'CAISO issues Black Start Activation Directive within 90 seconds of confirmed system islanding') nor pass/fail criterion; 'determine when... is required' is an internal cognitive act, not a verifiable system behavior. | Rewrite to specify a mandatory, time-bound, observable action triggered by a defined grid state.
kimi | R13 | U | Understandable | 3 | 0.8 | 证据片段：'The CAISO shall have the sole right to determine when the operation of Black Start Generating Unit is required...'。术语'Black Start Generating Unit'未在需求内定义，读者需外部知识才能完全理解，降低可理解性。 | 保持不变
kimi | R13 | A | Unambiguous | 2 | 0.9 | 证据片段：'conditions on the CAISO Controlled Grid'。'conditions'一词过于宽泛，未限定是电压异常、频率异常还是全黑状态，存在多种解释空间，导致歧义。 | CAISO shall have the sole authority to initiate Black Start Generating Unit operation upon detection of a total blackout or frequency below 59.0 Hz on the CAISO Controlled Grid.
kimi | R13 | C | Correctness | 4 | 0.9 | 证据片段：'the sole right to determine'。语法与业务主体一致，无自相矛盾，正确性尚可。 | 保持不变
kimi | R13 | V | Verifiable | 2 | 0.9 | 证据片段：'determine when...is required'。'determine'与'required'均为判断性动词，缺乏可观测的触发阈值或决策记录要求，无法通过测试或审查验证何时及为何做出决定。 | CAISO shall document in the Black Start Event Log the timestamp, measured grid condition values, and decision rationale each time it initiates Black Start Generating Unit operation.
glm5 | R13 | U | Understandable | 3 | 0.8 | 证据片段：'sole right to determine'。该表述属于商业契约或法律条款用语，而非技术需求规范。虽然语法通顺，但对于软件开发人员而言，缺乏具体的系统功能描述（如'系统应提供某按钮'或'系统应校验某权限'），理解成本较高。 | 保持不变（建议通过重写解决歧义问题）。
glm5 | R13 | A | Unambiguous | 2 | 0.9 | 证据片段：'sole right to determine when... is required'。该表述存在显著歧义：'right'在软件系统中未定义是'数据访问权限'、'操作权限'还是'业务决策权'；'determine'未指明是人工输入决策还是系统自动判断。这导致开发实施时存在多种解释。 | The System shall restrict the initiation of Black Start Generating Unit operations to CAISO authorized users.
glm5 | R13 | C | Correctness | 3 | 0.6 | 证据片段：'The CAISO shall have...'。作为软件需求，该条目描述的是组织机构的权利而非系统的行为或功能，属于业务需求层级，若作为系统需求则正确性存疑，因为软件系统无法'拥有权利'，只能'实现权限控制'。 | 保持不变（建议通过重写解决层级问题）。
glm5 | R13 | V | Verifiable | 2 | 0.9 | 证据片段：'determine when... is required'。该需求无法通过客观的测试用例验证。测试人员无法验证'权利'是否存在，也无法量化'何时被要求'的主观判断逻辑，缺乏明确的输入输出标准。 | The System shall provide a control interface for CAISO authorized users to trigger the Black Start Generating Unit operation.
qwen | R14 | U | Understandable | 2 | 0.9 | 'Each of he four points must reside in a different hour of the test' contains typo 'he' instead of 'the', impairing immediate readability; also 'hour of the test' is ambiguous—does it mean chronological time (e.g., real-time clock), test duration partition (e.g., 60-minute intervals), or execution phase? This undermines Understandability. | Replace with atomic, grammatically correct, and temporally grounded phrasing.
qwen | R14 | A | Unambiguous | 2 | 0.95 | 'a different hour of the test' lacks definition: no specification of test duration, start time, or whether 'hour' is literal (60 minutes) or metaphorical; 'reside' is vague verb for temporal placement—does it mean 'be scheduled', 'be executed', or 'be observed'? Thus unambiguous temporal binding is absent. | Specify exact temporal unit, reference point, and binding mechanism.
qwen | R14 | C | Correctness | 3 | 0.8 | The requirement may be technically correct if test duration ≥4 hours, but correctness cannot be assessed without knowing test length; however, no inconsistency with domain knowledge is evident, so score is moderate. | Keep unchanged pending domain confirmation, but add precondition on test duration.
qwen | R14 | V | Verifiable | 1 | 0.95 | No objective criterion for verification exists—no defined measurement method (e.g., timestamp logging), no pass/fail condition, and no observable artifact; 'must reside' is not testable as written—violates verifiability at fundamental level. | Rewrite to prescribe measurable behavior with pass/fail criteria.
kimi | R14 | U | Understandable | 3 | 0.8 | 原文'Each of he four points must reside in a different hour of the test'存在拼写错误'he'，且未定义'point'与'hour of the test'，读者需额外猜测含义，降低可理解性。 | 将'he'改为'the'，并明确定义术语：'The four measurement events shall each occur within a distinct 60-minute interval of the 4-hour test run.'
kimi | R14 | A | Unambiguous | 2 | 0.9 | 'point'与'hour of the test'在上下文中无唯一解释，可能指采样点、事件点或测试阶段，导致歧义。 | 用唯一术语替换'points'与'hour'：'The four measurement events shall each occur within a distinct 60-minute interval of the 4-hour test run.'
kimi | R14 | C | Correctness | 2 | 0.9 | 拼写错误'he'使句子语法失效；未说明测试总时长与小时划分方式，无法确认需求正确性。 | 修正拼写并补充上下文：'The four measurement events shall each occur within a distinct 60-minute interval of the 4-hour test run.'
kimi | R14 | V | Verifiable | 2 | 0.9 | 未给出'reside in a different hour'的可度量标准，测试人员无法验证四个点是否真正落在不同小时内。 | 给出可测标准：'Each of the four measurement events shall be timestamped and fall within a unique 60-minute interval (00:00–59:59, 01:00–01:59, 02:00–02:59, 03:00–03:59) of the test run; no two timestamps shall share the same interval.'
glm5 | R14 | U | Understandable | 3 | 0.9 | 证据片段：'Each of he four points'。原文存在明显的拼写错误（'he'应为'the'），导致阅读流畅度下降，虽然不影响大致理解，但降低了可读性。 | Each of the four data points must reside in a different hour of the test.
glm5 | R14 | A | Unambiguous | 2 | 0.8 | 证据片段：'four points' 和 'different hour'。'points' 指代不明（是数据点、得分点还是时间点？）；'different hour' 存在歧义，未明确是指时钟小时（如10:00-10:59）还是相对于测试开始的时长区间（如第1小时、第2小时）。 | Each of the four data points shall have a timestamp falling within a unique clock hour (e.g., HH:00 to HH:59) during the test execution.
glm5 | R14 | C | Correctness | 3 | 0.9 | 证据片段：'Each of he'。语法拼写错误属于正确性问题，需求文档应使用规范的语言。 | Each of the four points must reside in a different hour of the test.
glm5 | R14 | V | Verifiable | 2 | 0.8 | 证据片段：'reside in a different hour'。由于'points'定义缺失且'hour'界定模糊，无法设计确定的测试用例来验证需求是否满足。例如，若测试时长不足4小时该如何判定？ | The timestamps of the four data points shall fall into four distinct clock hours during the test execution.
qwen | R15 | U | Understandable | 2 | 0.9 | 'If… Then… The a Black Start unit did not successfully pass...' contains grammatical errors ('The a'), missing subject-verb agreement, and malformed conditional syntax; this impairs readability and parsing by stakeholders. Evidence: 'The a Black Start unit did not successfully pass' | If a Black Start unit fails to satisfy any mandatory item in Table 3.2 (Black Start Readiness Criteria), then the generator owner/operator shall submit a corrective action report to CAISO within 5 business days.
qwen | R15 | A | Unambiguous | 2 | 0.95 | 'Successfully pass the CAISO Black Start criteria specified in this procedure' is ambiguous: 'criteria' is plural but undefined—no reference to appendix, table, or versioned document; 'this procedure' lacks traceability. Evidence: 'CAISO Black Start criteria specified in this procedure' | If a Black Start unit receives a 'Not Compliant' rating for any mandatory item listed in Table 3.2 (Black Start Readiness Criteria, Rev. 2024-09), then...
qwen | R15 | C | Correctness | 3 | 0.8 | The requirement mandates an explanation and plan upon failure, which aligns with typical regulatory expectations; no factual contradiction is evident. Evidence: 'An explanation and a plan to address and correct the deficiency shall be provided to the CAISO by the generator owner/operator' | Keep unchanged
qwen | R15 | V | Verifiable | 1 | 0.95 | No objective pass/fail criterion is defined for 'successfully pass', nor are timing, format, content scope, or acceptance criteria for the 'explanation and plan' specified—making verification impossible. Evidence: 'An explanation and a plan to address and correct the deficiency shall be provided to the CAISO by the generator owner/operator' | The corrective action report shall include: (a) root cause analysis using the 5-Whys method; (b) corrective actions with assigned owners and due dates; (c) evidence of implementation for at least one action prior to submission; and (d) submission in PDF/A-1b format to CAISO via the Secure Portal before 17:00 PT on the fifth business day following notification of non-compliance.
kimi | R15 | U | Understandable | 3 | 0.8 | 原文以“If… Then…”开头，省略号未补全条件，读者需自行脑补触发场景，降低可读性。 | 保持不变
kimi | R15 | A | Unambiguous | 2 | 0.9 | “a Black Start unit”单复数混杂；“An explanation and a plan”未说明由谁负责撰写、格式、提交方式，存在解释空间。 | 将条件补全并明确单复数：'If a Black Start unit fails any CAISO Black Start criterion listed in Section X, then…'
kimi | R15 | C | Correctness | 3 | 0.7 | 未给出“CAISO Black Start criteria”的具体章节或文档编号，无法确认引用正确性。 | 保持不变
kimi | R15 | V | Verifiable | 2 | 0.9 | “successfully pass”“deficiency”“address and correct”均无量化标准，验收时无法客观判断通过与否。 | 保持不变
glm5 | R15 | U | Understandable | 2 | 0.9 | 证据片段：'If… Then… The a Black Start unit'。原文包含明显的语法错误 'The a' 以及残留的模板文本 'If… Then…'，严重破坏了句子的通顺性和可读性，导致理解困难。 | If a Black Start unit fails to pass the CAISO Black Start criteria specified in this procedure, the generator owner/operator shall provide an explanation and a corrective plan to the CAISO.
glm5 | R15 | A | Unambiguous | 3 | 0.8 | 证据片段：'The a Black Start unit'。双重冠词的使用导致主语指代不明（是特指某个单元还是泛指），虽然可以推断为泛指，但形式上存在歧义。 | If a Black Start unit fails to meet the CAISO Black Start criteria specified in this procedure, the generator owner/operator shall submit a detailed explanation and a corrective action plan to the CAISO.
glm5 | R15 | C | Correctness | 2 | 0.9 | 证据片段：'The a Black Start unit'。原文存在明显的语法错误，违反了自然语言的正确性规则，属于低级书写错误。 | If a Black Start unit does not successfully pass the CAISO Black Start criteria specified in this procedure, the generator owner/operator shall provide an explanation and a plan to address the deficiency to the CAISO.
glm5 | R15 | V | Verifiable | 3 | 0.7 | 证据片段：'An explanation and a plan'。虽然可以验证是否提交了文档，但未规定解释的详细程度和计划的具体内容要求（如是否需要包含时间表），导致验证'合格性'的标准主观性较强。 | If a Black Start unit fails the CAISO Black Start criteria, the generator owner/operator shall submit a written explanation and a corrective action plan to the CAISO.
qwen | R16 | U | Understandable | 2 | 0.9 | 'The results of the testing and the justification for the periodicity of the testing' is a compound noun phrase with ambiguous scope: it is unclear whether 'the justification' refers to the justification *for performing* the testing, or justification *for the chosen periodicity value*, and whether 'results' includes raw data, summary metrics, or compliance conclusions; this violates atomicity and increases cognitive load. | Split into two atomic requirements: one for test results, one for periodicity justification; define each artifact's required content explicitly.
qwen | R16 | A | Unambiguous | 2 | 0.95 | 'WECC or NERC' introduces logical ambiguity: does 'or' mean either organization may request (inclusive), or exactly one of them (exclusive)? Also, 'on request' lacks trigger definition—no specification of request format, authorized requester role, or whether verbal/written request suffices. | Replace 'WECC or NERC' with 'WECC or NERC (inclusive), acting through an authorized representative'; replace 'on request' with 'upon receipt of a written request signed by an authorized representative of WECC or NERC'.
qwen | R16 | C | Correctness | 3 | 0.8 | The requirement is broadly consistent with regulatory expectations for auditability, but 'periodicity of the testing' presumes a prior-defined testing schedule exists; if no such schedule is mandated elsewhere, this clause becomes circular or ungrounded—however, absence of explicit contradiction prevents lower correctness score. | Keep unchanged — the clause is not factually incorrect, though dependent on upstream schedule definition.
qwen | R16 | V | Verifiable | 1 | 0.95 | No objective pass/fail criterion is specified: 'provided' lacks definition of completeness (e.g., which fields must be included), format (PDF? CSV? API response?), delivery mechanism (email? portal upload?), nor acceptance criteria for 'within 30 days' (calendar days? business days? clock starts at receipt timestamp or request acknowledgment?). Thus, no test case can be constructed to verify compliance. | Rewrite as: 'Within 30 calendar days of receipt of a written request from an authorized representative of WECC or NERC, the system shall deliver via secure web portal a ZIP archive containing: (a) all raw test execution logs (in UTF-8 plain text), (b) a PDF report summarizing test outcomes and pass/fail status per test case ID, and (c) a signed statement justifying the selected testing interval (e.g., 90-day cycle) with reference to §X.Y of the applicable compliance standard.'
kimi | R16 | U | Understandable | 3 | 0.8 | 原文'results of the testing'未指明是原始数据、摘要报告还是签字版合规报告，读者需额外推断，降低可理解性。 | 将'results'具体化为'一份符合 WECC Reporting Template v3.2 的 PDF 测试总结报告'。
kimi | R16 | A | Unambiguous | 2 | 0.9 | 'testing'一词未限定是哪种测试（渗透测试、功能测试、回归测试等），且'justification for the periodicity'未说明需包含哪些论据，存在多种解释空间。 | 将'testing'明确为'每年度执行的内部网络安全渗透测试'；将'justification for the periodicity'明确为'包含风险评估矩阵与测试频率映射表的备忘录'。
kimi | R16 | C | Correctness | 3 | 0.7 | 未定义'provided'的具体形式（邮件、门户上传、纸质快递），也未说明'within 30 days'的起算点（收到请求日/次日/工作日），可能引发合规争议。 | 补充交付形式与起算点：'通过 WECC 安全门户上传，且上传完成日期不晚于请求送达后的第 30 个自然日'。
kimi | R16 | V | Verifiable | 2 | 0.9 | 无法通过单一事件确认'periodicity justification'是否充分，且'on request'使验证触发条件不确定，导致验收准则不可执行。 | 增加可测阈值：'报告须包含至少最近三次渗透测试的日期、执行人、漏洞数量及修复率；备忘录须说明年度风险等级≥High 的资产比例>5% 时测试频率为年度，否则为每 18 个月'。
glm5 | R16 | U | Understandable | 4 | 0.9 | 需求使用了'periodicity'等学术词汇，整体句式较长，但语义基本清晰。证据片段：'The results of the testing and the justification for the periodicity of the testing'。 | 保持不变
glm5 | R16 | A | Unambiguous | 3 | 0.8 | 时间约束'within 30 days'置于括号内，未明确说明起止时间点，存在歧义。证据片段：'on request (within 30 days)'。虽然通常理解为收到请求后，但作为需求规范不够严谨。 | The results of the testing and the justification for the periodicity of the testing shall be provided to WECC or NERC within 30 days of receiving a request.
glm5 | R16 | C | Correctness | 4 | 0.6 | 假设上下文为NERC合规标准，需求逻辑正确，符合合规性报告的常规流程。证据片段：'shall be provided to WECC or NERC'。 | 保持不变
glm5 | R16 | V | Verifiable | 3 | 0.8 | 'justification'缺乏具体的验收标准，导致难以客观验证理由是否充分。证据片段：'justification for the periodicity of the testing'。 | The results of the testing and a documented justification for the periodicity of the testing shall be provided to WECC or NERC within 30 days of receiving a request.
qwen | R17 | U | Understandable | 2 | 0.9 | 需求文本为长串无标点、无结构的文档引用列表，如'References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203...'，缺乏主谓宾结构和语义分隔，读者无法快速识别其功能意图或约束范围；未说明这些引用是'必须遵循''仅作参考'还是'需全部满足'，导致理解门槛高；证据片段：'References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203, Reliability Must Run Unit Commitment and Dispatch...' | 系统应确保所有黑启动发电单元的认证测试活动符合ISO Tariff Section 8.3.3、CAISO G-203、CAISO G-213、CAISO G-213H及CAISO G-213I的最新有效版本要求；
qwen | R17 | A | Unambiguous | 2 | 0.95 | 多个CAISO G-213相关条目（G-213、G-213H、G-213I）并列出现但未说明其关系（是否互斥？是否叠加？），且'NERC Reliability Standard EOP-005'与'EOP-009'之间缺少连接词，易引发歧义——例如EOP-009是否仅约束Blackstart Generating Unit Test Results的格式？证据片段：'NERC Reliability Standard EOP-005 System Restoration Plans EOP-009 Documentation of Blackstart Generating Unit Test Results' | 系统生成的黑启动测试报告必须包含EOP-009第4.2条规定的全部7个必填字段，并采用CAISO G-213H指定的PDF模板格式；
qwen | R17 | C | Correctness | 3 | 0.8 | 该需求未声明自身是合规性要求、设计约束还是信息性引用；未指明适用对象（如'所有黑启动机组'还是'新投运机组'），也未标注版本时效性（如'G-213H v2.1'），存在事实性遗漏风险；但因所列标准名称本身在行业属真实存在，故Correctness得分略高于其他维度。证据片段：'CAISO Operating Procedure G-213H Black Start Test Report Form' | 保持不变
qwen | R17 | V | Verifiable | 1 | 0.95 | 需求中无任何可观察、可测量的行为动词或判定准则，如'不得缺失EOP-009要求的6项字段'或'测试报告须在72小时内提交至CAISO Portal'；仅罗列标准名称，无法设计测试用例或验收检查表；证据片段：'References ISO Tariff Section 8.3.3 Certification and Testing Requirements...' | 系统应在用户提交黑启动测试报告后自动校验：① 文件名符合'BSR-{UnitID}-{YYYYMMDD}-vN.pdf'格式；② 元数据中包含EOP-009要求的TestDate、FuelType、StartSuccessRate字段且非空；③ 签章页含CAISO授权签字人数字签名。
kimi | R17 | U | Understandable | 2 | 0.9 | 证据片段：'References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203...'——整句仅为无动词的引用列表，缺少主语与谓语，读者无法判断'谁'必须'做什么'，导致可理解性低。 | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供对应合格报告。
kimi | R17 | A | Unambiguous | 2 | 0.9 | 证据片段：'References...'——未说明是'系统应遵守'还是'文档需包含'，也未限定适用范围（全部条款还是仅引用存在即可），存在多重解释空间。 | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供对应合格报告。
kimi | R17 | C | Correctness | 3 | 0.8 | 证据片段：整段引用列表——所列标准/程序本身正确，但需求未声明具体条款或版本，存在未来版本差异风险， correctness 中等。 | 系统须符合 CAISO Operating Procedure G-203 §8.3.3（2023版）的认证与测试要求，并在交付时提供对应合格报告。
kimi | R17 | V | Verifiable | 2 | 0.9 | 证据片段：'References...'——无验收条件（例如'须通过 CAISO G-213 规定的认证测试并提供合格报告'），测试人员无法判定合规，可验证性差。 | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供由 CAISO 签署的合格测试报告；验收测试将核查报告存在性及结论为'通过'。
glm5 | R17 | U | Understandable | 2 | 0.9 | 证据片段：'References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure...'。该文本仅为一系列名词短语的堆砌，缺乏标点符号、分隔符或列表结构，导致阅读困难，难以快速识别各个独立的引用文档。 | 使用项目符号或编号列表重新组织文档名称，并添加适当的标点符号。
glm5 | R17 | A | Unambiguous | 2 | 0.9 | 证据片段：'References'。该词作为需求描述的主体模糊不清，无法确定系统是需要'显示'这些引用、'符合'这些标准、还是'存储'这些文档名称，导致需求解释存在多种可能性。 | 将模糊的名词'References'替换为明确的系统行为动词，例如'系统应遵守'或'系统应提供以下文档的链接'。
glm5 | R17 | C | Correctness | 3 | 0.6 | 证据片段：'References ISO Tariff...'。虽然引用的文档名称可能属于领域内的正确术语，但需求条目本身语法结构不完整，缺乏主语和谓语，未能正确表达系统应实施的行为或应具备的属性。 | 将需求改写为完整的'主语+谓语+宾语'句式，确保需求描述的是系统的行为或约束。
glm5 | R17 | V | Verifiable | 1 | 1 | 证据片段：'References ISO Tariff...'。由于缺乏明确的动词（如'应显示'、'应遵守'），无法定义具体的测试步骤或通过标准，测试人员无法判断系统是否满足了该需求。 | 添加可验证的行为描述，例如'系统界面应包含以下参考文档列表'或'系统功能应符合以下标准要求'。

## ratings_r1
rater | item | dim | dimension | score | confidence | rationale | suggestion
qwen | R12 | U | Understandable | 3 | 0.95 | Grammatically sound and semantically clear: 'CAISO shall undertake performance tests' conveys responsibility and action. | No change needed.
qwen | R12 | A | Unambiguous | 3 | 0.95 | All terms are standard industry usage; 'performance tests' and 'prior notification' have widely accepted meanings in CAISO contexts. | No change needed.
qwen | R12 | C | Correctness | 3 | 0.9 | No conflict with other requirements. | No change needed.
qwen | R12 | V | Verifiable | 1 | 0.98 | 'From time to time' is inherently non-quantifiable and untestable — no minimum frequency, no upper bound, no definition of 'time' (calendar year? operational cycle?), preventing objective verification of compliance. | The CAISO shall execute and document results of at least one end-to-end contingency analysis validation test per calendar quarter, with all test inputs, configurations, and pass/fail determinations archived in the CAISO Compliance Repository within 24 hours of completion.
qwen | R13 | U | Understandable | 3 | 0.95 | Clear agent ('CAISO'), action ('determine'), and condition ('when... is required') — understandable as a delegation of authority. | No change needed.
qwen | R13 | A | Unambiguous | 1 | 0.98 | 'Determine when... is required' describes an internal decision process, not a system behavior; 'conditions on the CAISO Controlled Grid' is undefined (e.g., voltage collapse? frequency < 59.3 Hz? islanding event?) — leaving trigger conditions open to arbitrary interpretation. | Replace 'determine when the operation... is required' with 'initiate Black Start Generating Unit operation within 120 seconds of confirming any of the following grid conditions: (a) system islanding detected via loss of >95% of tie-line power flows for ≥5 seconds; (b) frequency falling below 59.3 Hz for ≥10 seconds'.
qwen | R13 | C | Correctness | 3 | 0.9 | No conflict with R12 or other dispatch-related requirements. | No change needed.
qwen | R13 | V | Verifiable | 1 | 0.98 | Decision-making is not observable or recordable unless mandated; absence of logging, timestamping, or rationale capture makes verification impossible — 'right to determine' is a legal assertion, not a testable system property. | Within 120 seconds of confirming a condition in U13.1, CAISO shall broadcast a Black Start Activation Directive via the CAISO Real-Time Messaging System (RTMS), logged with timestamp, directive ID, and triggering grid condition values in the Black Start Event Log.
qwen | R17 | U | Understandable | 1 | 0.99 | The requirement consists solely of an unstructured, unpunctuated list of document names — no verb, no subject, no grammatical predicate — violating basic readability conventions and imposing excessive cognitive load on readers to infer intent. | Rephrase as an active, subject-verb-object statement with clear agent ('The system shall...') and structured enumeration.
qwen | R17 | A | Unambiguous | 1 | 0.99 | Ambiguity is systemic: 'References' is not a behavioral verb and admits at least three interpretations ('must comply with', 'must display', 'must archive'); multiple CAISO G-213 variants (G-213, G-213H, G-213I) are listed without relational qualifiers (e.g., 'and', 'or', 'including'); EOP-005 and EOP-009 appear concatenated without conjunction, obscuring scope boundaries. | Replace 'References' with 'shall comply with and generate documentation satisfying' and append precise clause-level citations (e.g., 'CAISO G-213H §3.2 PDF template', 'EOP-009 §4.2 seven mandatory fields').
qwen | R17 | C | Correctness | 3 | 0.95 | No internal inconsistency — all cited documents pertain to black start certification and reporting. | No change needed.
qwen | R17 | V | Verifiable | 1 | 0.99 | Zero verifiable behavior: no observable output (e.g., report generation), no measurable state (e.g., field presence), no pass/fail criterion (e.g., signature validation), and no test method — making compliance assessment entirely subjective. | The system shall generate a black start test report PDF conforming to CAISO G-213H Appendix A, containing all seven EOP-009 §4.2 mandatory fields (TestDate, FuelType, StartSuccessRate, etc.) with non-empty values, and bearing a valid CAISO-authorized digital signature verified at runtime.
qwen | R2 | U | Understandable | 2 | 0.97 | Two independent clauses joined by period — acceptable but suboptimal; 'Such Test Dispatch Notice' lacks antecedent in this isolated requirement, reducing self-containment. | Replace 'Such Test Dispatch Notice' with 'The Black Start Test Dispatch Notice generated by the system' to establish clear antecedent.
qwen | R2 | A | Unambiguous | 1 | 0.99 | 'Shall be marked “Black Start Test Notice.”' omits critical qualifiers: location (subject line? header? watermark?), format (font, size, case sensitivity), and medium (email? PDF? API response?). 'In accordance with the Ancillary Services Requirements Protocol' fails to specify section number or version, inviting interpretation drift. | Specify marking location, font, size, and case: 'The dispatch notice PDF shall contain the exact visible text "Black Start Test Notice" centered in the top margin, in 16-point bold Arial font.' Also cite 'CAISO Tariff section 5.2.3 "Ancillary Services Requirements Protocol" (version 2024-03)'.
qwen | R2 | C | Correctness | 3 | 0.9 | No internal conflict. | No change needed.
qwen | R2 | V | Verifiable | 1 | 0.98 | No objective verification method: 'marked' is not observable without defining *how* and *where*; 'performed in accordance with' is untestable without binding, enumerated criteria (e.g., checklist items, timing constraints, output formats). | Upon initiation of a black start test dispatch, the system shall output a file named BS_TEST_NOTICE_YYYYMMDD_HHMMSS.pdf containing the exact string 'Black Start Test Notice' as the first non-whitespace text in the document, rendered in 16-point bold Arial font, and shall log the file generation timestamp and SHA-256 hash in the Audit Trail.
qwen | R6 | U | Understandable | 3 | 0.95 | The requirement is syntactically complete and uses standard technical terms ('Black Start unit', 'voltage', 'NERC reliability standards'); readers familiar with grid operations can grasp intent despite vagueness. | Retain current structure but add clarifying context (e.g., 'at the unit's point of interconnection') to anchor terminology.
qwen | R6 | A | Unambiguous | 1 | 0.98 | Critical terms lack binding definitions: 'emergency voltage limits' is undefined and appears in multiple NERC standards (BAL-003, TOP-004, PRC-024) with conflicting tolerances; 'in accordance with NERC reliability standards' fails to specify standard ID, version, or clause — enabling divergent interpretations across reviewers and auditors. | Replace 'emergency voltage limits' with '±10% of nominal voltage at the high-side bus, per NERC BAL-003-3 Section 4.2.1 (Effective Date: 2023-07-01)' and explicitly cite the governing standard.
qwen | R6 | C | Correctness | 3 | 0.9 | No internal contradictions; all clauses coherently describe a single functional capability. | No change needed.
qwen | R6 | V | Verifiable | 1 | 0.98 | No testable pass/fail criteria: no numeric voltage bounds, no defined load points (e.g., 0%/50%/100%), no dwell time, no measurement location (e.g., high-side bus), and no instrumentation class — rendering verification impossible without external interpretation. | The Black Start unit shall maintain voltage at its high-side bus within ±10% of nominal voltage for ≥30 seconds under each of the following steady-state loading conditions: (a) 0.0 MW ± 0.1 MW, (b) 50 MW ± 0.1 MW, (c) 100% of rated active power, measured using Class 0.2 voltage transducers.
qwen | R9 | U | Understandable | 3 | 0.95 | Clear subject ('Black Start unit'), verb ('must be capable'), and object ('starting and energizing...') — intent is immediately discernible. | No change needed.
qwen | R9 | A | Unambiguous | 1 | 0.99 | 'Applicable transmission path' is undefined (no identifier, no configuration reference); 'without assistance from the electrical system' is critically ambiguous — does it exclude only AC grid power, or also DC control batteries, auxiliary generators, or communication links? NERC PRC-024 defines 'black start capability' as requiring *zero external AC power*, but this is not reflected here. | Replace 'applicable transmission path' with 'the 230 kV Main Export Line between Black Start Unit and Grid Substation A' and 'without assistance from the electrical system' with 'using only on-site, non-grid-dependent energy sources (i.e., dedicated black start diesel generator and/or battery bank supplying control and prime mover power), with zero AC voltage or power input from the external electrical grid'.
qwen | R9 | C | Correctness | 3 | 0.9 | No contradiction with other black start requirements. | No change needed.
qwen | R9 | V | Verifiable | 3 | 0.95 | Capability is verifiable via test protocol (e.g., islanded startup test), provided 'applicable path' and 'assistance' are precisely bounded. | No change needed — verifiability becomes achievable once ambiguity is resolved.
qwen | R1 | U | Understandable | 2 | 0.9 | 'They must be able to self-start without any source of off-site electric power' lacks subject identification — 'They' is ambiguous (generators? control systems? black-start units?) and violates atomicity; readers cannot determine scope without external context. | Replace with subject-explicit, atomic statement: 'Each designated black-start generator shall initiate its own startup sequence using only on-site energy sources (e.g., batteries, diesel starters, or flywheels), without connection to off-site AC power.'
qwen | R1 | A | Unambiguous | 2 | 0.95 | 'self-start', 'adequate voltage and frequency', and 'isolated transmission facilities' are undefined terms — 'adequate' is subjective, 'isolated transmission facilities' has no boundary specification (voltage level? topology? length?), introducing interpretation variance. | Define all critical terms quantitatively and contextually: 'self-start' → 'achieve rated speed and synchronize within 300 seconds'; 'adequate voltage and frequency' → 'maintain terminal voltage within ±5% of 13.8 kV and system frequency within ±0.05 Hz'; 'isolated transmission facilities' → 'the 138-kV radial feeder segment between Bus A and Substation X, de-energized from the bulk grid and loaded only by the black-start generator and its connected auxiliary loads.'
qwen | R1 | C | Correctness | 3 | 0.8 | The requirement logically aligns with black-start capability standards (e.g., NERC BAL-003), but 'auxiliary loads of other generators' implies cross-generator dependency during islanded operation, which contradicts typical black-start sequencing where only the initiating unit powers its own auxiliaries first; this may reflect a domain misconception. | Revise to reflect correct operational sequence: 'During black-start, the generator shall energize only its own auxiliary loads and the designated isolated transmission facility; it shall not supply auxiliary loads of other generators until those generators have achieved synchronized, stable operation.'
qwen | R1 | V | Verifiable | 1 | 0.98 | No testable thresholds or conditions are provided — e.g., no numeric values for voltage (±% of nominal?), frequency (Hz tolerance?), duration (how long must stability be maintained?), nor defined test configuration (which loads? how many MW? what fault clearance time?). Without these, verification is impossible. | Provide measurable pass/fail criteria: 'Within 60 seconds of synchronization, the generator shall maintain voltage at 13.8 kV ±5% and frequency at 60.00 Hz ±0.05 Hz for ≥300 seconds while supplying a minimum load of 2.5 MW (comprising its own auxiliaries and the isolated 138-kV feeder).'
qwen | R3 | U | Understandable | 2 | 0.85 | 'constrained water availability' is a vague, context-dependent qualitative phrase without defined thresholds or measurement method; readers cannot consistently interpret when it applies — evidence: 'periods of constrained water availability'. | Replace with objectively bounded definition using measurable hydrologic parameters.
qwen | R3 | A | Unambiguous | 2 | 0.9 | 'constrained water availability' admits multiple interpretations (e.g., reservoir level < X%, inflow < Y cfs, drought declaration status); absence of objective criteria makes the condition ambiguous — evidence: 'constrained water availability'. | Define 'constrained water availability' as a Boolean condition based on publicly reported, time-stamped data sources.
qwen | R3 | C | Correctness | 3 | 0.75 | The requirement is plausibly correct from operational safety perspective, but lacks traceability to regulatory source (e.g., CAISO Tariff Section 22.3 or FERC Order 881) and does not specify whether this applies to all hydro units or only those designated as black start resources — evidence: 'The CAISO shall not request a Black Start Test for a hydroelectric Unit during periods of constrained water availability'. | Add reference to governing regulation and scope qualifier (e.g., 'for hydroelectric units designated as Black Start Resources per Appendix D of CAISO Tariff').
qwen | R3 | V | Verifiable | 1 | 0.95 | No testable condition is provided: there is no defined metric, threshold, time window, or authoritative data source to determine if 'constrained water availability' holds at a given moment; thus, verification requires subjective judgment — evidence: 'periods of constrained water availability'. | Specify verifiable trigger: e.g., 'when the applicable federal or state drought declaration is active AND the unit's primary reservoir elevation falls below 85% of its normal pool elevation, as reported in real-time by USGS gauge ID XXXX'.
qwen | R4 | U | Understandable | 2 | 0.9 | 'Demonstrate at least every five years, through simulation or testing' is vague about scope and method; 'any request' and 'any past reports' lack temporal bounds and scope definition, impairing reader's ability to grasp required actions without external interpretation; the nested bullet 'o Those Participants who do not currently test...' introduces unstructured conditional logic that breaks atomicity and obscures applicability. | Split into atomic, subject-verb-object requirements; replace all conditionals ('if any', 'who do not currently') with explicit scope definitions; eliminate nested bullets and use numbered clauses.
qwen | R4 | A | Unambiguous | 2 | 0.95 | 'Demonstrate... as required by the WECC BCP (if any)' introduces ambiguity: 'if any' makes compliance contingent on unknown existence of a document; 'success or failure of the test' is undefined—no criteria provided for determining either outcome; 'notify... by phone indicating the success or failure' conflates communication modality with functional outcome assessment. | Replace 'if any' with 'as specified in the latest approved edition of the WECC Black Start Capability Procedure (WECC BCP)'; define 'success' as 'full restoration of black start capability per Section 4.2 of WECC BCP-2023' and 'failure' as 'inability to achieve any step in the validated black start sequence within tolerance limits'; replace 'notify... indicating success or failure' with 'transmit a standardized status code (BS-OK or BS-FAIL) via CAISO's designated real-time notification channel'.
qwen | R4 | C | Correctness | 3 | 0.8 | The requirement states Participants 'will be required to test' if they 'do not currently test'—but this is a procedural directive, not a verifiable condition; no normative source confirms this obligation exists in current CAISO/WECC/NERC rules, and 'will be required' is future-tense prescriptive language inconsistent with a requirements specification (which should state what *is* required, not what *will be*). | Replace 'will be required to test their Black Start capability' with 'shall perform an initial black start capability test no later than 180 days after this requirement becomes effective, per Section 5.1 of CAISO Tariff Appendix V'.
qwen | R4 | V | Verifiable | 2 | 0.85 | No objective pass/fail criteria are defined for 'success or failure'; 'within 24 hours' and 'within 14 days' are testable, but 'submit documentation of the test results and analysis to the CAISO, WECC, or NERC upon any request' cannot be verified because 'any request' is non-deterministic and unbounded—there is no trigger condition or observable event that defines when the requirement applies. | Replace 'upon any request' with 'within 5 business days of receipt of a written request from CAISO, WECC, or NERC'; replace 'success or failure of the test' with 'a signed test report containing timestamped evidence of all 7 mandatory sequence steps (per WECC BCP Table 3.1), each annotated with measured voltage/frequency/timing values and deviation tolerances'.
qwen | R5 | U | Understandable | 3 | 0.8 | 'an indication of whether the tests met the requirements of this Black Start Testing section' is abstract and lacks concrete criteria for 'indication' — e.g., pass/fail flag, textual summary, or compliance code; users may interpret it as a checkbox, a narrative comment, or a reference to external documentation, reducing immediate comprehensibility. | Replace with atomic, concrete phrasing specifying data format and intent.
qwen | R5 | A | Unambiguous | 2 | 0.9 | 'an indication of whether the tests met the requirements' is ambiguous: it does not specify *which* requirements (e.g., all? only functional? only safety-critical?) nor define the evaluation basis (e.g., objective pass/fail against acceptance criteria, or subjective engineering judgment). The phrase 'this Black Start Testing section' is circular if the requirement itself resides in that section. | Specify exact compliance scope and unambiguous representation.
qwen | R5 | C | Correctness | 4 | 0.95 | The requirement correctly mandates inclusion of dates, duration, and compliance status — consistent with typical test record expectations for regulatory traceability; no factual or domain-logic error is evident. | 保持不变
qwen | R5 | V | Verifiable | 2 | 0.9 | 'an indication of whether the tests met the requirements' is not testable: there is no defined pass/fail criterion, no specified format (e.g., Boolean field 'compliance_status: true/false'), and no measurable success condition — an auditor cannot objectively verify compliance without knowing what constitutes valid 'indication' or which requirements are being assessed. | Replace with a verifiable, binary, and format-constrained statement.
qwen | R7 | U | Understandable | 2 | 0.85 | 'capable of operating in an isochronous mode' is vague and lacks context for non-expert readers; no definition of 'isochronous mode' is provided, nor whether it applies to all load conditions or only specific ones — this reduces Understandability. | Replace with atomic, self-contained definition: 'The Black Start unit's governor shall maintain system frequency within ±0.02 Hz of 50 Hz (or 60 Hz, per site specification) when operating in islanded mode with no external grid reference and under load steps from 0% to 100% rated output.'
qwen | R7 | A | Unambiguous | 2 | 0.9 | 'capable of operating' introduces ambiguity: does it mean the governor must support isochronous mode by design, or must it be configured and verified to operate in that mode during black start? The phrase fails to specify activation condition, scope (e.g., frequency range, response time), or functional boundary — violating Unambiguity. | Specify mandatory configuration and activation: 'The governor shall be pre-configured and locked in isochronous control mode prior to black start initiation, and shall remain in that mode throughout the black start sequence until grid synchronization.'
qwen | R7 | C | Correctness | 3 | 0.75 | The requirement aligns with standard black start practices where isochronous control is typical for initial grid restoration; no evidence contradicts technical correctness, though it omits dependency on unit type (e.g., hydro vs. gas turbine) — hence moderate score. | Keep unchanged — but add traceability note in rationale: 'This reflects IEEE 1547-2018 Annex D and NERC PRC-006-2 requirements for islanded frequency regulation during restoration.'
qwen | R7 | V | Verifiable | 1 | 0.95 | No testable criterion is given: no measurable parameter (e.g., frequency deviation ≤ ±0.02 Hz under 0–100% load step), no test condition (e.g., 'during simulated islanded operation with no external grid reference'), and no pass/fail threshold — making verification impossible as written. | Add verifiable acceptance criteria: 'During factory acceptance test (FAT), the governor shall demonstrate frequency regulation within ±0.02 Hz of nominal (50/60 Hz) for three consecutive 20% load steps (0→20→40→60%) in islanded mode, measured using calibrated PMU; deviation exceeding ±0.05 Hz at any 100-ms interval shall constitute failure.'
qwen | R8 | U | Understandable | 2 | 0.85 | 'Adequate transmission capacity' is vague and lacks quantifiable criteria; users cannot determine what 'adequate' means without context or thresholds — evidence: 'Adequate transmission capacity shall be available'; | Specify minimum rated capacity (in MVA) and voltage level for the transmission path between the Black Start facility and its designated station service source;
qwen | R8 | A | Unambiguous | 2 | 0.9 | 'Adequate' is inherently subjective and context-dependent; 'the source providing station services to other specified generating stations' is ambiguous about which source (e.g., specific substation, voltage level, or grid node) — evidence: 'the source providing station services to other specified generating stations'; | Replace 'Adequate transmission capacity' with 'Transmission capacity rated ≥ 25 MVA at 34.5 kV' and identify the station service source as 'Substation SS-BS01, Bus B2, per Appendix A';
qwen | R8 | C | Correctness | 3 | 0.75 | The requirement does not contradict known black start standards (e.g., NERC PRC-002), but omits critical technical constraints like voltage level, fault current contribution, or thermal limits — evidence: no mention of voltage class, duration, or system interface point; | Keep unchanged pending system architecture review; however, add dependency on R3 (Grid Interface Specification) to ensure consistency;
qwen | R8 | V | Verifiable | 1 | 0.95 | No testable criterion is provided: no measurable quantity (e.g., MW, MVA, kV), no acceptance threshold, no defined test condition or method — evidence: 'shall be available' is non-falsifiable and unverifiable without metrics or conditions; | Rewrite to require demonstrable capacity via steady-state load flow analysis showing ≤ 5% voltage drop and ≥ 1.2 pu short-circuit ratio at the interconnection point under N-1 contingency.
qwen | R10 | U | Understandable | 2 | 0.9 | 'Hot, steam-driven turbines, within 2.5 hours' lacks subject-verb agreement and omits 'shall start' or equivalent verb; the bullet list mixes noun phrases ('Hydroelectric generating units...') with incomplete clauses, impairing readability and comprehension for non-native speakers and reviewers. The phrase 'If the certified Black Start facility is in another reliability coordinator area or is comprised of an unspecified technology then specific start time limits are negotiated' uses passive voice and vague terms ('negotiated', 'unspecified technology') without defining responsible party or timeframe, reducing understandability. | The Black Start testing units shall achieve full synchronization with the grid within the following maximum elapsed times after the official initiation signal: (a) hydroelectric generating units and combustion gas turbines: 30 minutes; (b) industrial gas turbines: 60 minutes; (c) steam-driven turbine units operating in hot standby mode: 2.5 hours; (d) all other certified Black Start facilities: a time limit mutually agreed upon in writing by the Reliability Coordinator and the facility owner prior to testing.
qwen | R10 | A | Unambiguous | 2 | 0.95 | 'Hot, steam-driven turbines' is ambiguous: does it mean 'turbines that are hot' (thermal state) or 'turbines driven by hot steam' (design type)? Also, 'unspecified technology' is inherently ambiguous—no criteria define what constitutes 'unspecified'; 'reliability coordinator area' is undefined in this requirement and may vary across jurisdictions, introducing interpretation variance. | Keep unchanged
qwen | R10 | C | Correctness | 3 | 0.8 | The requirement appears technically plausible for black start timing categories, and no internal contradiction or factual error is evident from domain knowledge (e.g., steam units typically require longer warm-up); however, 'Hot, steam-driven turbines' may incorrectly imply operational readiness state rather than unit type—potentially conflating condition with classification—so correctness is moderate pending clarification. | Replace 'Hot, steam-driven turbines' with 'steam-driven turbine units operating in hot standby mode' to align with NERC PRC-005-6 terminology and avoid conflation of thermal state with unit category.
qwen | R10 | V | Verifiable | 1 | 0.95 | No test procedure, measurement method, or pass/fail criterion is specified: e.g., 'within 30 minutes' lacks definition of 'initiation' (clock start trigger), 'start-up/synchronizing time' is not defined (is it first rotation? grid synchronization? stable power delivery?), and 'negotiated' time limits are untestable by objective means. Absence of measurable observables makes verification impossible per ISO/IEC/IEEE 29148. | For each unit type, the elapsed time shall be measured from the timestamp of the official Black Start initiation command (issued by the Reliability Coordinator) to the timestamp of verified, stable grid synchronization (defined as sustained 60 Hz frequency ±0.05 Hz and voltage within ±5% of nominal for ≥30 seconds), recorded by a calibrated, tamper-evident data acquisition system.
qwen | R11 | U | Understandable | 2 | 0.9 | 'All Black Start Generating Units' lacks definition — 'Black Start Generating Units' is undefined and context-dependent; readers cannot determine scope without external domain knowledge. Evidence: 'All Black Start Generating Units'. | Define 'Black Start Generating Unit' as a generating unit certified by CAISO for black start service per CAISO Tariff Section 27.3(a)(1), capable of initiating energization without off-site power.
qwen | R11 | A | Unambiguous | 2 | 0.95 | 'must satisfy technical requirements specified by the CAISO' is ambiguous because 'technical requirements' is a non-specific reference to an external, unversioned, and unbounded document set; no identifier, version, or clause is provided. Evidence: 'technical requirements specified by the CAISO'. | Replace with: 'Each Black Start Generating Unit shall comply with all mandatory technical criteria in CAISO Tariff Appendix D, Revision 4.2 (effective 2023-09-15), Sections D.1 through D.5.'
qwen | R11 | C | Correctness | 3 | 0.8 | The requirement does not contradict known CAISO practice (CAISO does regulate black start units), so correctness is plausible; however, absence of normative source citation reduces confidence. Evidence: 'must satisfy technical requirements specified by the CAISO'. | Keep unchanged — but add normative reference: 'as defined in CAISO Tariff Section 27.3'.
qwen | R11 | V | Verifiable | 1 | 0.95 | No testable criterion is stated — e.g., no measurable parameter, pass/fail condition, or verification method (e.g., document review, functional test, certification audit). Evidence: 'must satisfy technical requirements' — satisfaction is undefined and unobservable. | Each Black Start Generating Unit shall demonstrate compliance via submission of a valid CAISO Black Start Certification Letter issued within the prior 12 months, verified by the System Operator during unit registration.
qwen | R14 | U | Understandable | 2 | 0.9 | 'Each of he four points must reside in a different hour of the test' contains typo 'he' instead of 'the', impairing immediate readability; also 'hour of the test' is ambiguous—does it mean chronological time (e.g., real-time clock), test duration partition (e.g., 60-minute intervals), or execution phase? This undermines Understandability. | Replace with atomic, grammatically correct, and temporally grounded phrasing.
qwen | R14 | A | Unambiguous | 2 | 0.95 | 'a different hour of the test' lacks definition: no specification of test duration, start time, or whether 'hour' is literal (60 minutes) or metaphorical; 'reside' is vague verb for temporal placement—does it mean 'be scheduled', 'be executed', or 'be observed'? Thus unambiguous temporal binding is absent. | Specify exact temporal unit, reference point, and binding mechanism.
qwen | R14 | C | Correctness | 3 | 0.8 | The requirement may be technically correct if test duration ≥4 hours, but correctness cannot be assessed without knowing test length; however, no inconsistency with domain knowledge is evident, so score is moderate. | Keep unchanged pending domain confirmation, but add precondition on test duration.
qwen | R14 | V | Verifiable | 1 | 0.95 | No objective criterion for verification exists—no defined measurement method (e.g., timestamp logging), no pass/fail condition, and no observable artifact; 'must reside' is not testable as written—violates verifiability at fundamental level. | Rewrite to prescribe measurable behavior with pass/fail criteria.
qwen | R15 | U | Understandable | 2 | 0.9 | 'If… Then… The a Black Start unit did not successfully pass...' contains grammatical errors ('The a'), missing subject-verb agreement, and malformed conditional syntax; this impairs readability and parsing by stakeholders. Evidence: 'The a Black Start unit did not successfully pass' | If a Black Start unit fails to satisfy any mandatory item in Table 3.2 (Black Start Readiness Criteria), then the generator owner/operator shall submit a corrective action report to CAISO within 5 business days.
qwen | R15 | A | Unambiguous | 2 | 0.95 | 'Successfully pass the CAISO Black Start criteria specified in this procedure' is ambiguous: 'criteria' is plural but undefined—no reference to appendix, table, or versioned document; 'this procedure' lacks traceability. Evidence: 'CAISO Black Start criteria specified in this procedure' | If a Black Start unit receives a 'Not Compliant' rating for any mandatory item listed in Table 3.2 (Black Start Readiness Criteria, Rev. 2024-09), then...
qwen | R15 | C | Correctness | 3 | 0.8 | The requirement mandates an explanation and plan upon failure, which aligns with typical regulatory expectations; no factual contradiction is evident. Evidence: 'An explanation and a plan to address and correct the deficiency shall be provided to the CAISO by the generator owner/operator' | Keep unchanged
qwen | R15 | V | Verifiable | 1 | 0.95 | No objective pass/fail criterion is defined for 'successfully pass', nor are timing, format, content scope, or acceptance criteria for the 'explanation and plan' specified—making verification impossible. Evidence: 'An explanation and a plan to address and correct the deficiency shall be provided to the CAISO by the generator owner/operator' | The corrective action report shall include: (a) root cause analysis using the 5-Whys method; (b) corrective actions with assigned owners and due dates; (c) evidence of implementation for at least one action prior to submission; and (d) submission in PDF/A-1b format to CAISO via the Secure Portal before 17:00 PT on the fifth business day following notification of non-compliance.
qwen | R16 | U | Understandable | 2 | 0.9 | 'The results of the testing and the justification for the periodicity of the testing' is a compound noun phrase with ambiguous scope: it is unclear whether 'the justification' refers to the justification *for performing* the testing, or justification *for the chosen periodicity value*, and whether 'results' includes raw data, summary metrics, or compliance conclusions; this violates atomicity and increases cognitive load. | Split into two atomic requirements: one for test results, one for periodicity justification; define each artifact's required content explicitly.
qwen | R16 | A | Unambiguous | 2 | 0.95 | 'WECC or NERC' introduces logical ambiguity: does 'or' mean either organization may request (inclusive), or exactly one of them (exclusive)? Also, 'on request' lacks trigger definition—no specification of request format, authorized requester role, or whether verbal/written request suffices. | Replace 'WECC or NERC' with 'WECC or NERC (inclusive), acting through an authorized representative'; replace 'on request' with 'upon receipt of a written request signed by an authorized representative of WECC or NERC'.
qwen | R16 | C | Correctness | 3 | 0.8 | The requirement is broadly consistent with regulatory expectations for auditability, but 'periodicity of the testing' presumes a prior-defined testing schedule exists; if no such schedule is mandated elsewhere, this clause becomes circular or ungrounded—however, absence of explicit contradiction prevents lower correctness score. | Keep unchanged — the clause is not factually incorrect, though dependent on upstream schedule definition.
qwen | R16 | V | Verifiable | 1 | 0.95 | No objective pass/fail criterion is specified: 'provided' lacks definition of completeness (e.g., which fields must be included), format (PDF? CSV? API response?), delivery mechanism (email? portal upload?), nor acceptance criteria for 'within 30 days' (calendar days? business days? clock starts at receipt timestamp or request acknowledgment?). Thus, no test case can be constructed to verify compliance. | Rewrite as: 'Within 30 calendar days of receipt of a written request from an authorized representative of WECC or NERC, the system shall deliver via secure web portal a ZIP archive containing: (a) all raw test execution logs (in UTF-8 plain text), (b) a PDF report summarizing test outcomes and pass/fail status per test case ID, and (c) a signed statement justifying the selected testing interval (e.g., 90-day cycle) with reference to §X.Y of the applicable compliance standard.'
kimi | R1 | U | Understandable | 3 | 0.75 | 原文使用'They'未指明主体，'adequate voltage and frequency'未给出数值范围，降低可理解性 | 将'They'替换为'每台应急黑启动燃气轮机'，并补充'电压偏差≤±5 %额定值，频率偏差≤±0.5 Hz'
kimi | R1 | A | Unambiguous | 2 | 0.8 | 'self-start''adequate''isolated transmission facilities'等术语缺乏唯一解释，存在多种理解可能 | 定义：'self-start'='在厂用电全失且无任何外部电源情况下，于30 min内完成机组启动并带初始负载'；'isolated transmission facilities'='本厂220 kV升压站及下游空充线路总长≤100 km'
kimi | R1 | C | Correctness | 3 | 0.7 | 未限定启动条件（环境温度、燃料状态）及负载阶跃，无法判断需求是否物理可行 | 补充前提：'在环境温度-10 °C至45 °C、燃料罐液位≥30 %、润滑系统预润滑完成条件下'
kimi | R1 | V | Verifiable | 2 | 0.85 | 'adequate'无量化指标，'maintain'未给出持续时间与容许偏差，测试无法判定通过/失败 | 增加可测试指标：'黑启动后0→25 %额定负载阶跃，电压恢复时间≤5 s，频率瞬变≤±1 Hz，稳态频率偏差≤±0.2 Hz，持续运行≥4 h'
kimi | R2 | U | Understandable | 3 | 0.8 | 原文出现'Such Test Dispatch Notice'，但未在前文定义该术语，读者需回溯才能理解'Such'指代何物，降低可读性 | 将'Such Test Dispatch Notice'替换为显式定义后的名称，如'Black Start Test Dispatch Notice'
kimi | R2 | A | Unambiguous | 2 | 0.9 | 短语'in accordance with the Ancillary Services Requirements Protocol in the CAISO Tariff'未给出具体章节/条款编号，不同人可能定位到不同版本或不同段落，存在解释差异 | 补充精确引用，如'CAISO Tariff第5.2.3节Ancillary Services Requirements Protocol(版本2024-03)'
kimi | R2 | C | Correctness | 4 | 0.7 | 需求仅引用外部协议，未明确若协议更新是否自动适用；一旦CAISO Tariff变更，需求正确性可能失效 | 增加冻结条款，如'以CAISO Tariff 2024-03版为准，若后续版本有冲突，以本需求发布日有效版本优先'
kimi | R2 | V | Verifiable | 2 | 0.9 | 未定义可观察的验证标准，如'marked'是否仅要求页眉出现指定文字、'performed in accordance with'如何判定合规，测试人员无法设计通过/失败准则 | 增加可测标准，如'在PDF页眉居中打印“Black Start Test Notice”，字体Arial 12pt；测试步骤与结果须100%符合CAISO Tariff第5.2.3节表A要求，由独立审计员出具合规报告'
kimi | R3 | U | Understandable | 3 | 0.8 | 原文使用'constrained water availability'这一非专业口语化短语，未给出定义或量化阈值，导致不同角色理解差异，降低可理解性。 | CAISO不得在水库可用水量低于日常最小发电需水量对应水位时，要求水电机组进行黑启动试验。
kimi | R3 | A | Unambiguous | 2 | 0.7 | 'periods of constrained water availability'无明确判定标准，无法确定何时触发禁止，存在多种解释空间，造成歧义。 | CAISO不得在水库水位≤EL. 120 m或收到水务调度'限水运行'指令期间，要求水电机组进行黑启动试验。
kimi | R3 | C | Correctness | 3 | 0.6 | 未说明'constrained'由谁、依据何种规则认定；若未来水资源管理政策变化，需求可能失效，正确性风险高。 | CAISO不得在水库水位≤EL. 120 m或收到水务调度'限水运行'指令期间，要求水电机组进行黑启动试验。
kimi | R3 | V | Verifiable | 2 | 0.7 | 缺少可测指标（如水库水位、入库流量、调度令号等），测试人员无法客观验证'constrained'状态是否成立，从而无法验证需求是否被满足。 | CAISO不得在水库水位≤EL. 120 m或收到水务调度'限水运行'指令期间，要求水电机组进行黑启动试验。
kimi | R4 | U | Understandable | 3 | 0.7 | 原文使用多层嵌套列表与口语化短语'if any'，读者需自行拆解'Demonstrate…that the unit can perform its intended functions'等长句，增加理解成本。 | 将长句拆分为独立原子需求，每条只含一个义务主体、动作、频率、交付物。
kimi | R4 | A | Unambiguous | 3 | 0.7 | 'its intended functions'未指明具体功能清单；'Participants who do not currently test'范围模糊；'success or failure'未定义判定准则，存在多种解释。 | 用唯一术语替换'Participants'，明确'intended functions'对应WECC BCP表X条款Y；定义'success'为≥90%关键参数在表Z限值内。
kimi | R4 | C | Correctness | 3 | 0.7 | 未说明当WECC BCP不存在时是否仍需演示；'any past reports'未限定时间范围，可能要求提交几十年前失效报告，与法规一致性存疑。 | 增加前提条件：仅当WECC BCP适用时执行对应条款；'past reports'限定为最近10年且仍有效。
kimi | R4 | V | Verifiable | 3 | 0.7 | 'Demonstrate through simulation or testing'未规定测试场景、通过阈值及记录格式；'notify…by phone'未要求留痕，无法客观验证是否按时完成。 | 为每条验证活动补充可测标准：测试方案须提前30天提交CAISO备案；电话通知后1小时内发送带时间戳的邮件确认；报告模板采用CAISO-BS-14表格。
kimi | R5 | U | Understandable | 4 | 0.8 | 句子结构清晰，关键词'dates、duration、indication'易于理解，但'an indication of whether the tests met the requirements'未说明指示形式，略损可理解性。 | 保持不变
kimi | R5 | A | Unambiguous | 2 | 0.6 | 'an indication of whether the tests met the requirements'未定义指示的格式、取值或判定规则，存在多种解释空间。 | 将'an indication of whether the tests met the requirements'替换为'a Boolean field “testPassed” with value true if all applicable Black Start Test cases defined in Section X.Y pass, otherwise false'。
kimi | R5 | C | Correctness | 3 | 0.7 | 未明确'duration'的计量单位、时区、精度；'dates'是否含起止；'met the requirements'未引用具体条款，无法确认正确性边界。 | 在'duration'后补充'expressed in whole seconds in UTC'；在'dates'后补充'in ISO-8601 format with start and end timestamps'；并引用具体条款编号。
kimi | R5 | V | Verifiable | 2 | 0.6 | 'indication'未规定可测值（如Pass/Fail布尔值、代码、百分比），导致验证时缺乏客观判据。 | 同A维度改写，使验证只需检查布尔字段值。
kimi | R6 | U | Understandable | 3 | 0.8 | 短语'emergency voltage limits'与'in accordance with NERC reliability standards'未给出具体数值或标准条款，读者需额外查阅外部文档才能理解完整要求 | The Black Start unit shall maintain its output voltage between 0.95 pu and 1.05 pu while supplying active power from 0 % to 100 % of its nameplate rating, as defined in NERC PRC-024-2 clause 4.3.
kimi | R6 | A | Unambiguous | 2 | 0.9 | 'emergency voltage limits'与'full external load'未定义具体数值或百分比，存在多种解释空间；'NERC reliability standards'未指明具体条款 | The Black Start unit shall maintain its output voltage between 0.95 pu and 1.05 pu while supplying active power from 0 % to 100 % of its nameplate rating, as defined in NERC PRC-024-2 clause 4.3.
kimi | R6 | C | Correctness | 3 | 0.7 | 需求未说明'Black Start unit'指柴油发电机、储能还是其他类型，无法判断其技术可行性是否满足NERC标准 | The Black Start diesel generator shall maintain its output voltage between 0.95 pu and 1.05 pu while supplying active power from 0 % to 100 % of its nameplate rating, as defined in NERC PRC-024-2 clause 4.3.
kimi | R6 | V | Verifiable | 2 | 0.9 | 未给出可测量的电压带、负载步长、测试持续时间和允差，测试人员无法设计验证用例 | During factory acceptance test, the Black Start unit shall be stepped from 0 % to 25 %, 50 %, 75 % and 100 % of nameplate active power; voltage shall remain within 0.95–1.05 pu for ≥5 min at each step with maximum 2 % overshoot and recovery time ≤2 s.
kimi | R7 | U | Understandable | 3 | 0.7 | 原文使用'Black Start unit'与'governors'等术语，但未给出定义或范围，读者需额外背景知识才能理解 | 保持不变
kimi | R7 | A | Unambiguous | 3 | 0.7 | 'Black Start unit'未指明是单台机组还是一类机组；'equipped with governors'未说明是物理安装还是功能具备；'capable of operating'未给出判定条件 | 保持不变
kimi | R7 | C | Correctness | 3 | 0.7 | 未引用任何标准或法规来界定'isochronous mode'的技术要求，无法判断需求是否完整正确 | 保持不变
kimi | R7 | V | Verifiable | 3 | 0.7 | 未给出验证场景、验收准则或量化指标，测试人员无法设计可重复的验证步骤 | 保持不变
kimi | R8 | U | Understandable | 3 | 0.8 | 原文使用'Adequate transmission capacity'与'station services'等术语，但未给出容量阈值或服务范围，导致不同角色理解差异，降低可理解性。 | 保持术语但补充定义：'Black Start facility'指具备黑启动能力的XX MW燃机站；'station services'指厂用电负荷。
kimi | R8 | A | Unambiguous | 2 | 0.8 | 'Adequate'与'other specified generating stations'均未量化或枚举，无法确定'足够'标准及'指定'清单，存在显著歧义。 | 将'Adequate'改为'≥150 MVA连续输送能力'；将'other specified generating stations'枚举为'A站、B站、C站'。
kimi | R8 | C | Correctness | 3 | 0.7 | 需求未说明'transmission capacity'所属电压等级、持续时间或N-1准则，无法判断其正确性与完整性。 | 补充技术条件：在最高环境温度40 ℃、单回线路N-1停运情况下，输送能力仍满足≥150 MVA。
kimi | R8 | V | Verifiable | 2 | 0.8 | 无容量数值、测试条件及观测点，验收时无法设计测试用例验证'capacity shall be available'。 | 增加验收条款：在Black Start试验期间，测量线路首末端功率，15分钟平均值≥150 MVA，持续2小时无设备过载报警。
kimi | R9 | U | Understandable | 3 | 0.8 | 原文'applicable transmission path'未指明具体路径，读者需额外上下文才能理解范围，降低直观性。 | 将'applicable transmission path'替换为具体线路名称或电压等级范围。
kimi | R9 | A | Unambiguous | 2 | 0.9 | 'applicable'与'without assistance'均未定义判定准则，可因不同解读产生歧义。 | 删除'applicable'并给出唯一路径标识；将'without assistance'限定为'零外部电源输入'。
kimi | R9 | C | Correctness | 3 | 0.7 | 未给出'starting'与'energizing'的电压/时间阈值，无法判断需求是否技术上可行或完整。 | 补充'在30分钟内将线路电压升至≥230 kV并保持≥15分钟'等量化指标。
kimi | R9 | V | Verifiable | 2 | 0.9 | 缺乏可观测指标（如电压等级、建立时间、允许的最大外部能量），测试人员无法设计验证步骤。 | 增加可测条件：'在试验中记录黑启动机组输出功率、线路电压曲线，且全程无外部电源输入'。
kimi | R10 | U | Understandable | 3 | 0.7 | 原文使用'start-up/synchronizing time limits'并列，未明确是'启动'还是'并网'，且'initiation of the Black Start process'未定义触发事件，降低可读性。 | 将'start-up/synchronizing time limits'拆分为两条独立需求：启动完成时间、并网完成时间，并定义'Black Start process initiation'为'调度员下达黑启动指令瞬间'。
kimi | R10 | A | Unambiguous | 3 | 0.7 | 'unspecified technology then specific start time limits are negotiated'未指明由谁、何时、如何谈判，存在多方解释空间。 | 删除'negotiated'，改为'由系统调度机构与机组业主在测试计划书中书面约定启动完成时间，且该时间≤4小时'。
kimi | R10 | C | Correctness | 3 | 0.7 | 未给出'Hot, steam-driven turbines'的温度阈值，也未说明'certified Black Start facility'的认证标准，无法判断正确性。 | 补充'Hot'定义：'主蒸汽压力≥8 MPa且温度≥500 °C'；引用认证标准如NERC BAL-005。
kimi | R10 | V | Verifiable | 3 | 0.7 | 'negotiated'结果无定量指标，测试人员无法设计通过/失败准则，导致不可验证。 | 所有机组类型均给出单一数值时限，删除谈判条款，使测试用例可直接比对实测分钟数。
kimi | R11 | U | Understandable | 3 | 0.8 | 原文'All Black Start Generating Units must satisfy technical requirements specified by the CAISO'中未定义'Black Start Generating Unit'，读者需额外背景知识才能理解。 | 将'Black Start Generating Unit'替换为'能够在全站失电后无需外部电源、于30分钟内带动厂用负荷并具备向电网送电能力的机组'。
kimi | R11 | A | Unambiguous | 2 | 0.9 | 'technical requirements specified by the CAISO'未指明具体文档或版本，存在多种解释空间。 | 将'technical requirements specified by the CAISO'替换为'CAISO Technical Bulletin 2023-01《Black Start Unit Certification Criteria》第4-7节'。
kimi | R11 | C | Correctness | 2 | 0.8 | 未给出CAISO技术要求的有效版本或发布日期，可能随时间变化导致需求失效。 | 在需求中引用'CAISO Technical Bulletin 2023-01（生效日期2023-06-01）'并注明版本锁定策略。
kimi | R11 | V | Verifiable | 1 | 0.95 | 无量化指标或测试步骤，无法设计用例验证是否'满足'要求。 | 增加可测试条款：'机组应在型式试验中于30分钟内完成黑启动并建立≥5%额定电压，试验报告须由CAISO认可的第三方出具'。
kimi | R12 | U | Understandable | 3 | 0.8 | 短语'from time to time'未给出任何周期或触发条件，读者无法判断测试频率，降低可理解性。 | CAISO shall execute performance tests at least once per calendar quarter.
kimi | R12 | A | Unambiguous | 2 | 0.9 | 'with or without prior notification'在同一句话内并列两种完全相反的情形，未说明何时需提前通知、何时可免，存在明显歧义。 | CAISO may conduct performance tests either (a) with no less than 10 business days prior written notice, or (b) without notice when required for emergency reliability assessment.
kimi | R12 | C | Correctness | 3 | 0.7 | 需求仅声明CAISO'shall undertake'，未定义测试通过/失败标准、范围或最低覆盖率，无法判断 correctness 的达成条件。 | Each performance test shall cover no less than 80 % of critical-path transactions and achieve ≤ 2 second 95th-percentile response time to be deemed successful.
kimi | R12 | V | Verifiable | 1 | 0.95 | 无量化指标（频率、通知时限、测试类型、通过准则），测试人员无法设计验证步骤，基本不可验证。 | Compliance is verified by (i) quarterly test execution records, (ii) dated notification emails, and (iii) test reports showing ≥ 80 % coverage and ≤ 2 s 95th-percentile response time.
kimi | R13 | U | Understandable | 3 | 0.8 | 证据片段：'The CAISO shall have the sole right to determine when the operation of Black Start Generating Unit is required...'。术语'Black Start Generating Unit'未在需求内定义，读者需外部知识才能完全理解，降低可理解性。 | 保持不变
kimi | R13 | A | Unambiguous | 2 | 0.9 | 证据片段：'conditions on the CAISO Controlled Grid'。'conditions'一词过于宽泛，未限定是电压异常、频率异常还是全黑状态，存在多种解释空间，导致歧义。 | CAISO shall have the sole authority to initiate Black Start Generating Unit operation upon detection of a total blackout or frequency below 59.0 Hz on the CAISO Controlled Grid.
kimi | R13 | C | Correctness | 4 | 0.9 | 证据片段：'the sole right to determine'。语法与业务主体一致，无自相矛盾，正确性尚可。 | 保持不变
kimi | R13 | V | Verifiable | 2 | 0.9 | 证据片段：'determine when...is required'。'determine'与'required'均为判断性动词，缺乏可观测的触发阈值或决策记录要求，无法通过测试或审查验证何时及为何做出决定。 | CAISO shall document in the Black Start Event Log the timestamp, measured grid condition values, and decision rationale each time it initiates Black Start Generating Unit operation.
kimi | R14 | U | Understandable | 3 | 0.8 | 原文'Each of he four points must reside in a different hour of the test'存在拼写错误'he'，且未定义'point'与'hour of the test'，读者需额外猜测含义，降低可理解性。 | 将'he'改为'the'，并明确定义术语：'The four measurement events shall each occur within a distinct 60-minute interval of the 4-hour test run.'
kimi | R14 | A | Unambiguous | 2 | 0.9 | 'point'与'hour of the test'在上下文中无唯一解释，可能指采样点、事件点或测试阶段，导致歧义。 | 用唯一术语替换'points'与'hour'：'The four measurement events shall each occur within a distinct 60-minute interval of the 4-hour test run.'
kimi | R14 | C | Correctness | 2 | 0.9 | 拼写错误'he'使句子语法失效；未说明测试总时长与小时划分方式，无法确认需求正确性。 | 修正拼写并补充上下文：'The four measurement events shall each occur within a distinct 60-minute interval of the 4-hour test run.'
kimi | R14 | V | Verifiable | 2 | 0.9 | 未给出'reside in a different hour'的可度量标准，测试人员无法验证四个点是否真正落在不同小时内。 | 给出可测标准：'Each of the four measurement events shall be timestamped and fall within a unique 60-minute interval (00:00–59:59, 01:00–01:59, 02:00–02:59, 03:00–03:59) of the test run; no two timestamps shall share the same interval.'
kimi | R15 | U | Understandable | 3 | 0.8 | 原文以“If… Then…”开头，省略号未补全条件，读者需自行脑补触发场景，降低可读性。 | 保持不变
kimi | R15 | A | Unambiguous | 2 | 0.9 | “a Black Start unit”单复数混杂；“An explanation and a plan”未说明由谁负责撰写、格式、提交方式，存在解释空间。 | 将条件补全并明确单复数：'If a Black Start unit fails any CAISO Black Start criterion listed in Section X, then…'
kimi | R15 | C | Correctness | 3 | 0.7 | 未给出“CAISO Black Start criteria”的具体章节或文档编号，无法确认引用正确性。 | 保持不变
kimi | R15 | V | Verifiable | 2 | 0.9 | “successfully pass”“deficiency”“address and correct”均无量化标准，验收时无法客观判断通过与否。 | 保持不变
kimi | R16 | U | Understandable | 3 | 0.8 | 原文'results of the testing'未指明是原始数据、摘要报告还是签字版合规报告，读者需额外推断，降低可理解性。 | 将'results'具体化为'一份符合 WECC Reporting Template v3.2 的 PDF 测试总结报告'。
kimi | R16 | A | Unambiguous | 2 | 0.9 | 'testing'一词未限定是哪种测试（渗透测试、功能测试、回归测试等），且'justification for the periodicity'未说明需包含哪些论据，存在多种解释空间。 | 将'testing'明确为'每年度执行的内部网络安全渗透测试'；将'justification for the periodicity'明确为'包含风险评估矩阵与测试频率映射表的备忘录'。
kimi | R16 | C | Correctness | 3 | 0.7 | 未定义'provided'的具体形式（邮件、门户上传、纸质快递），也未说明'within 30 days'的起算点（收到请求日/次日/工作日），可能引发合规争议。 | 补充交付形式与起算点：'通过 WECC 安全门户上传，且上传完成日期不晚于请求送达后的第 30 个自然日'。
kimi | R16 | V | Verifiable | 2 | 0.9 | 无法通过单一事件确认'periodicity justification'是否充分，且'on request'使验证触发条件不确定，导致验收准则不可执行。 | 增加可测阈值：'报告须包含至少最近三次渗透测试的日期、执行人、漏洞数量及修复率；备忘录须说明年度风险等级≥High 的资产比例>5% 时测试频率为年度，否则为每 18 个月'。
kimi | R17 | U | Understandable | 2 | 0.9 | 证据片段：'References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203...'——整句仅为无动词的引用列表，缺少主语与谓语，读者无法判断'谁'必须'做什么'，导致可理解性低。 | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供对应合格报告。
kimi | R17 | A | Unambiguous | 2 | 0.9 | 证据片段：'References...'——未说明是'系统应遵守'还是'文档需包含'，也未限定适用范围（全部条款还是仅引用存在即可），存在多重解释空间。 | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供对应合格报告。
kimi | R17 | C | Correctness | 3 | 0.8 | 证据片段：整段引用列表——所列标准/程序本身正确，但需求未声明具体条款或版本，存在未来版本差异风险， correctness 中等。 | 系统须符合 CAISO Operating Procedure G-203 §8.3.3（2023版）的认证与测试要求，并在交付时提供对应合格报告。
kimi | R17 | V | Verifiable | 2 | 0.9 | 证据片段：'References...'——无验收条件（例如'须通过 CAISO G-213 规定的认证测试并提供合格报告'），测试人员无法判定合规，可验证性差。 | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供由 CAISO 签署的合格测试报告；验收测试将核查报告存在性及结论为'通过'。
glm5 | R1 | U | Understandable | 3 | 0.9 | 证据片段：'They must be able to...'。代词 'They' 缺乏明确的先行词，读者必须依赖上下文推测主语，且句子结构较长，增加了认知负荷。 | 将代词 'They' 替换为具体的系统组件名称，并将长句拆分为两个独立的原子需求。
glm5 | R1 | A | Unambiguous | 2 | 0.9 | 证据片段：'adequate voltage and frequency'。形容词 'adequate'（充足的）是主观判断，未定义具体的数值范围或标准，导致不同开发者理解不一致。证据片段：'They'。主语指代不明。 | 将 'adequate' 替换为具体的数值范围或引用具体标准，明确主语。
glm5 | R1 | C | Correctness | 3 | 0.6 | 证据片段：'maintain adequate voltage and frequency'。由于缺乏具体的阈值或引用标准，无法判断该需求是否符合电网规范或设备技术规格，正确性无法保证。 | 引用具体的行业标准（如 IEEE 或 IEC 标准）来界定电压和频率的合格范围。
glm5 | R1 | V | Verifiable | 2 | 0.9 | 证据片段：'adequate voltage and frequency'。由于缺乏可量化的数值（如 '220V±5%' 或 '50Hz±0.2Hz'），测试人员无法设计测试用例来客观地判定通过或失败。 | 将 'adequate' 替换为具体的、可测量的数值范围。
glm5 | R2 | U | Understandable | 3 | 0.9 | 证据片段：“Such Test Dispatch Notice”。使用了指示代词“Such”指代前文内容，导致该条目在孤立阅读时主语不明确，降低了理解的直观性。 | 系统应将测试调度通知标记为“Black Start Test Notice”。
glm5 | R2 | A | Unambiguous | 2 | 0.9 | 证据片段：“shall be marked”。未指明标记的具体位置（如邮件主题、文档页眉、系统字段）和方式，导致实现方式存在歧义。 | 系统应在测试调度通知的【通知类型】字段中显示“Black Start Test Notice”。
glm5 | R2 | C | Correctness | 4 | 0.5 | 证据片段：“Ancillary Services Requirements Protocol in the CAISO Tariff”。假设引用的外部协议存在且正确，该需求在业务逻辑上是成立的，但缺乏对具体规则的直接描述。 | 保持不变。
glm5 | R2 | V | Verifiable | 2 | 0.9 | 证据片段：“performed in accordance with”。属于典型的“按引用包含”，若不获取并解析外部协议的具体内容，无法编写具体的测试用例来验证是否合规。 | 系统应依据《CAISO Tariff》中《Ancillary Services Requirements Protocol》规定的步骤执行黑启动测试，并生成执行日志。
glm5 | R3 | U | Understandable | 3 | 0.8 | 证据片段：'periods of constrained water availability'。虽然句子结构清晰，但关键条件短语缺乏明确的业务定义，不同读者可能对其含义产生不同的理解，影响了整体的可理解性。 | The CAISO shall not request a Black Start Test for a hydroelectric Unit during periods defined as 'constrained water availability' in the Water Management Policy.
glm5 | R3 | A | Unambiguous | 2 | 0.9 | 证据片段：'periods of constrained water availability'。该短语存在显著歧义，未定义'constrained'的具体阈值或判定标准（如水位百分比、流量限制或官方公告），导致无法明确界定触发条件。 | The CAISO shall not request a Black Start Test for a hydroelectric Unit when the reservoir water level is below [Specific Threshold]% or when a drought emergency is declared by [Authority].
glm5 | R3 | C | Correctness | 3 | 0.6 | 证据片段：'The CAISO shall not request...'。需求描述的逻辑关系在语法上是正确的，符合一般业务逻辑，但缺乏具体定义可能导致实际执行偏离真实业务意图，因此给予中等分数。 | 保持不变
glm5 | R3 | V | Verifiable | 2 | 0.9 | 证据片段：'periods of constrained water availability'。由于缺乏可量化的指标（如具体水位数值）或明确的触发事件，测试人员无法客观判定系统是否处于该状态，导致需求不可验证。 | The CAISO shall not request a Black Start Test for a hydroelectric Unit when the reservoir water level is below [Specific Threshold]% or when a drought emergency is declared by [Authority].
glm5 | R4 | U | Understandable | 3 | 0.9 | 需求使用了嵌套的项目符号（'o Those Participants...'）且主语在 'owner or operator' 和 'Participants' 之间切换，导致逻辑结构混乱，难以快速识别责任主体。证据片段：'The owner or operator... shall... o Those Participants who do not currently test...'。 | 将嵌套的项目符号独立为单独的条目，并统一使用 'The Participant' 或 'The owner/operator' 作为主语，保持一致性。
glm5 | R4 | A | Unambiguous | 2 | 0.9 | 存在多处模糊表达：'any past reports' 未定义时间范围；'will be required to test' 缺乏明确的截止时间或触发条件；'intended functions' 缺乏具体定义。证据片段：'Submit any past reports'、'will be required to test'、'perform its intended functions'。 | 将 'any past reports' 修改为具体的时间范围（如 'past 5 years'）；将 'will be required to test' 修改为具体的行动要求（如 'shall conduct a test within X days'）。
glm5 | R4 | C | Correctness | 3 | 0.8 | 原文中 'required by the WECC BCP (if any) and of this testing section' 存在明显的语法错误，介词 'of' 使用不当，影响对需求正确性的理解。证据片段：'required by the WECC BCP (if any) and of this testing section'。 | 修正语法错误，将 'and of this testing section' 改为 'and the requirements of this testing section'。
glm5 | R4 | V | Verifiable | 3 | 0.8 | 虽然部分条款（如 'Within 24 hours'）可验证，但核心性能要求 'perform its intended functions' 缺乏具体的量化标准或验收准则，导致无法客观验证测试是否通过。证据片段：'perform its intended functions'。 | 引用具体的性能标准文档或列出具体的测试通过标准（如启动时间、持续时长等），替换 'perform its intended functions'。
glm5 | R5 | U | Understandable | 4 | 0.9 | 证据片段：'Testing records shall include the dates of the tests...'。句子语法结构清晰，使用了标准的'shall'语气，易于读者理解大致意图。 | 保持不变
glm5 | R5 | A | Unambiguous | 2 | 0.9 | 证据片段：'dates of the tests' 和 'an indication of whether the tests met the requirements'。'dates'未指明是开始日期、结束日期还是执行日期；'indication'未定义具体格式（如布尔值、枚举字符串或自由文本），导致实现歧义。 | Testing records shall include the start date and time of each test, the duration of each test in minutes, and a test result status of 'Pass' or 'Fail' indicating compliance with the requirements of this Black Start Testing section.
glm5 | R5 | C | Correctness | 4 | 0.6 | 证据片段：'Testing records shall include...'。假设业务背景为标准的测试记录管理，要求记录时间、时长和结果是符合逻辑且正确的，无明显错误。 | 保持不变
glm5 | R5 | V | Verifiable | 2 | 0.9 | 证据片段：'duration of the tests' 和 'indication'。'duration'缺少时间单位（如分钟或小时），无法精确验证数值是否符合预期；'indication'缺少明确的通过/失败判定标准或数据格式，导致验证测试无法编写明确的断言。 | Testing records shall include the start date and time of each test, the duration of each test in minutes, and a test result status of 'Pass' or 'Fail' indicating compliance with the requirements of this Black Start Testing section.
glm5 | R6 | U | Understandable | 4 | 0.9 | 句子结构清晰，使用了'The Black Start unit'、'maintain voltage'等标准术语，语法通顺，易于阅读理解。 | 保持不变
glm5 | R6 | A | Unambiguous | 2 | 0.9 | 证据片段'in accordance with NERC reliability standards'存在歧义，NERC标准众多，未指明具体标准编号及版本；证据片段'emergency voltage limits'未定义具体数值范围，导致不同读者可能产生不同理解。 | The Black Start unit shall maintain voltage within the High and Low Emergency Voltage limits defined in Table X (e.g., 0.95 p.u. to 1.05 p.u.) over a range of loading from no external load to full external load, in accordance with NERC PRC-024-2.
glm5 | R6 | C | Correctness | 3 | 0.8 | 需求描述的功能逻辑在领域内通常是正确的，但由于引用了笼统的'NERC reliability standards'，无法确认其是否精确引用了适用的特定技术条款，存在引用错误的风险。 | The Black Start unit shall maintain voltage within [Specific Voltage Range] over a range of loading from no external load to full external load, complying with the specific requirements of NERC [Standard ID].
glm5 | R6 | V | Verifiable | 2 | 1 | 证据片段'emergency voltage limits'缺乏具体的数值定义，且'range of loading'未指定测试的具体负载点，导致测试人员无法设计明确的通过/失败判定标准。 | The Black Start unit shall maintain terminal voltage between [Min Voltage] and [Max Voltage] when the external load is varied from 0% to 100% of rated capacity in steps of [Step Value], as verified against the criteria in NERC [Standard ID].
glm5 | R7 | U | Understandable | 4 | 0.9 | 文本使用了标准的工程术语，语法结构清晰，易于理解。证据片段：'Black Start unit'、'governors'、'isochronous mode'。 | 保持不变。
glm5 | R7 | A | Unambiguous | 4 | 0.8 | 术语 'isochronous mode' 在控制工程领域有标准定义（恒定频率控制），'capable of' 指明了能力要求，语义相对明确。证据片段：'isochronous mode'。 | 保持不变。
glm5 | R7 | C | Correctness | 3 | 0.9 | 使用了 'must' 而非需求工程标准关键词 'shall'。根据 ISO/IEC/IEEE 29148 标准，'shall' 应用于定义强制性需求，'must' 通常用于描述自然规律或不可违背的约束，此处用法不规范。证据片段：'must be equipped'。 | The Black Start unit shall be equipped with governors that are capable of operating in an isochronous mode.
glm5 | R7 | V | Verifiable | 3 | 0.8 | 需求缺乏具体的验收标准。'capable of operating' 仅描述了能力，未定义在该模式下运行的性能指标（如频率稳定性、负载调整率），导致验证测试缺乏明确的通过准则。证据片段：'capable of operating in an isochronous mode'。 | The Black Start unit shall be equipped with governors capable of isochronous operation, maintaining a steady-state frequency deviation within ±[X] Hz under [Y]% load steps.
glm5 | R8 | U | Understandable | 3 | 0.8 | 证据片段：'connect the Black Start facility to the source providing station services to other specified generating stations'。句子嵌套层级过深，需多次解析'source providing...'的修饰关系才能理解连接对象，增加了认知负荷。 | 将长句拆分为多个短句，明确连接路径。例如：'Transmission capacity shall connect the Black Start facility to the station service source. This source shall supply services to the generating stations listed in [Reference ID].'
glm5 | R8 | A | Unambiguous | 2 | 0.9 | 证据片段：'Adequate transmission capacity'、'specified generating stations'。'Adequate'是主观形容词，缺乏量化标准；'specified'指代不明，未说明是在何处指定的，导致需求存在多种解释。 | 将模糊词汇替换为具体参数或引用。例如：'The transmission capacity shall be at least [X] MW.'
glm5 | R8 | C | Correctness | 3 | 0.6 | 证据片段：'source providing station services'。虽然逻辑上看似合理，但由于缺乏上下文引用，无法确认'specified generating stations'的列表是否存在于其他文档中，影响了需求的完整性和正确性。 | 补充缺失的引用或定义。例如：'...to generating stations specified in [Document ID, Section X].'
glm5 | R8 | V | Verifiable | 2 | 0.9 | 证据片段：'Adequate transmission capacity'、'shall be available'。由于没有定义'Adequate'的具体数值阈值（如MW数）或标准，测试人员无法客观判断容量是否满足要求；'available'也未定义可用性状态的具体条件。 | 增加可量化的验收标准。例如：'The transmission capacity between [Point A] and [Point B] shall be verified to be greater than or equal to [X] MW under [Condition Y].'
glm5 | R9 | U | Understandable | 4 | 0.9 | 证据片段：'Black Start unit'、'transmission path'。使用了标准的电力工程术语，句子结构清晰，但对于非领域专家可能存在理解门槛，整体可读性良好。 | 保持不变。
glm5 | R9 | A | Unambiguous | 2 | 0.9 | 证据片段：'applicable transmission path'、'without assistance'。'applicable'未定义具体指哪条路径，导致范围模糊；'without assistance'未界定'协助'的具体形式（如功率辅助、控制信号辅助等），存在多种解释。 | The Black Start unit shall start and energize the transmission path defined in [System_Configuration_Data] while isolated from the external electrical grid.
glm5 | R9 | C | Correctness | 4 | 0.6 | 证据片段：'starting and energizing... without assistance from the electrical system'。该描述符合'黑启动'的标准定义，即在不依赖外部电网支持的情况下恢复供电，逻辑上正确。 | 保持不变。
glm5 | R9 | V | Verifiable | 2 | 0.9 | 证据片段：'capable of'、'without assistance'。'capable of'描述的是一种潜能而非具体动作，难以直接测试；'without assistance'缺乏量化标准，无法设计明确的通过/失败准则。 | The Black Start unit shall start and energize the designated transmission path within [Time_Limit] seconds without drawing power from the external electrical grid.
glm5 | R10 | U | Understandable | 4 | 0.9 | 证据片段：'start-up/synchronizing time limits'。使用斜杠'/'连接两个术语，导致语义不清，读者难以判断是指'启动时间'与'同步时间'两个独立指标，还是指'从启动到同步的时间'。 | 将'start-up/synchronizing time limits'修改为'start-up to synchronizing time limits'，明确时间起止点。
glm5 | R10 | A | Unambiguous | 2 | 0.9 | 证据片段：'Hot, steam-driven turbines' 和 'specific start time limits are negotiated'。'Hot'缺乏明确定义（如具体的温度阈值或停机时长），导致状态判断歧义；'negotiated'描述的是一个过程而非确定的结果，导致需求执行标准模糊。 | 定义'Hot'的具体参数（例如：停机时间小于X小时或金属温度高于Y度）；将'negotiated'改为要求明确记录数值的强制性条款。
glm5 | R10 | C | Correctness | 3 | 0.6 | 证据片段：'specific start time limits are negotiated'。从需求工程角度看，需求应规定明确的约束条件，而非描述'协商'这一行为过程，这可能导致需求交付物缺失具体的验收标准，影响需求的正确性。 | 将'negotiated'替换为具体的文档引用或默认值设定，确保需求包含确定的约束。
glm5 | R10 | V | Verifiable | 2 | 0.9 | 证据片段：'Hot, steam-driven turbines' 和 'negotiated'。由于'Hot'状态未量化，测试人员无法客观判定设备是否处于该状态；'negotiated'未指定协商结果的存储位置或生效条件，导致无法验证最终的时间限制是否符合要求。 | 补充'Hot'的量化定义，并要求'negotiated'的结果必须记录在指定文档中以便验证。
glm5 | R11 | U | Understandable | 4 | 0.9 | 证据片段：'All Black Start Generating Units must satisfy...'。句子语法结构清晰，使用了标准的行业术语，对于领域专家而言易于理解。 | 保持不变。
glm5 | R11 | A | Unambiguous | 2 | 0.9 | 证据片段：'technical requirements specified by the CAISO'。'technical requirements' 指代过于宽泛，未指明具体文档、版本号或条款号，导致需求范围界定模糊，存在歧义。 | All Black Start Generating Units must satisfy the technical requirements specified in 'CAISO Tariff Section [X]' or 'BPM for Managing Full Frequency Response', Version [Y].
glm5 | R11 | C | Correctness | 3 | 0.6 | 证据片段：'specified by the CAISO'。在没有外部领域知识验证 CAISO 是否确实规定了这些要求的情况下，无法完全确认其正确性，但逻辑上符合业务语境。 | 保持不变。
glm5 | R11 | V | Verifiable | 2 | 0.9 | 证据片段：'satisfy technical requirements'。由于缺乏具体的量化指标或明确的引用文档，测试人员无法构建具体的测试用例来判断是否满足要求。 | All Black Start Generating Units must satisfy the technical requirements specified in 'CAISO Tariff Section [X]' or 'BPM for Managing Full Frequency Response', Version [Y].
glm5 | R12 | U | Understandable | 4 | 0.9 | 证据片段'from time to time'虽然语法通顺且易于阅读，但语义较为模糊，读者难以把握具体的执行频率，影响了理解的精确性。 | 保持不变。
glm5 | R12 | A | Unambiguous | 2 | 0.95 | 证据片段'from time to time'属于模糊量词，缺乏明确的定义或量化标准，导致不同读者对测试频率产生不同的解释，存在明显歧义。 | The CAISO shall undertake performance tests at least once per calendar year, with or without prior notification.
glm5 | R12 | C | Correctness | 3 | 0.6 | 需求描述了主体行为，但在缺乏业务背景的情况下，无法确认模糊的频率描述是否准确反映了业务意图或合规要求，存在正确性风险。 | The CAISO shall undertake performance tests at least once per calendar year, with or without prior notification.
glm5 | R12 | V | Verifiable | 2 | 0.95 | 证据片段'from time to time'无法被客观度量或计数，测试人员无法设计明确的通过/失败标准来验证该需求是否已被满足。 | The CAISO shall undertake performance tests at least once per calendar year, with or without prior notification.
glm5 | R13 | U | Understandable | 3 | 0.8 | 证据片段：'sole right to determine'。该表述属于商业契约或法律条款用语，而非技术需求规范。虽然语法通顺，但对于软件开发人员而言，缺乏具体的系统功能描述（如'系统应提供某按钮'或'系统应校验某权限'），理解成本较高。 | 保持不变（建议通过重写解决歧义问题）。
glm5 | R13 | A | Unambiguous | 2 | 0.9 | 证据片段：'sole right to determine when... is required'。该表述存在显著歧义：'right'在软件系统中未定义是'数据访问权限'、'操作权限'还是'业务决策权'；'determine'未指明是人工输入决策还是系统自动判断。这导致开发实施时存在多种解释。 | The System shall restrict the initiation of Black Start Generating Unit operations to CAISO authorized users.
glm5 | R13 | C | Correctness | 3 | 0.6 | 证据片段：'The CAISO shall have...'。作为软件需求，该条目描述的是组织机构的权利而非系统的行为或功能，属于业务需求层级，若作为系统需求则正确性存疑，因为软件系统无法'拥有权利'，只能'实现权限控制'。 | 保持不变（建议通过重写解决层级问题）。
glm5 | R13 | V | Verifiable | 2 | 0.9 | 证据片段：'determine when... is required'。该需求无法通过客观的测试用例验证。测试人员无法验证'权利'是否存在，也无法量化'何时被要求'的主观判断逻辑，缺乏明确的输入输出标准。 | The System shall provide a control interface for CAISO authorized users to trigger the Black Start Generating Unit operation.
glm5 | R14 | U | Understandable | 3 | 0.9 | 证据片段：'Each of he four points'。原文存在明显的拼写错误（'he'应为'the'），导致阅读流畅度下降，虽然不影响大致理解，但降低了可读性。 | Each of the four data points must reside in a different hour of the test.
glm5 | R14 | A | Unambiguous | 2 | 0.8 | 证据片段：'four points' 和 'different hour'。'points' 指代不明（是数据点、得分点还是时间点？）；'different hour' 存在歧义，未明确是指时钟小时（如10:00-10:59）还是相对于测试开始的时长区间（如第1小时、第2小时）。 | Each of the four data points shall have a timestamp falling within a unique clock hour (e.g., HH:00 to HH:59) during the test execution.
glm5 | R14 | C | Correctness | 3 | 0.9 | 证据片段：'Each of he'。语法拼写错误属于正确性问题，需求文档应使用规范的语言。 | Each of the four points must reside in a different hour of the test.
glm5 | R14 | V | Verifiable | 2 | 0.8 | 证据片段：'reside in a different hour'。由于'points'定义缺失且'hour'界定模糊，无法设计确定的测试用例来验证需求是否满足。例如，若测试时长不足4小时该如何判定？ | The timestamps of the four data points shall fall into four distinct clock hours during the test execution.
glm5 | R15 | U | Understandable | 2 | 0.9 | 证据片段：'If… Then… The a Black Start unit'。原文包含明显的语法错误 'The a' 以及残留的模板文本 'If… Then…'，严重破坏了句子的通顺性和可读性，导致理解困难。 | If a Black Start unit fails to pass the CAISO Black Start criteria specified in this procedure, the generator owner/operator shall provide an explanation and a corrective plan to the CAISO.
glm5 | R15 | A | Unambiguous | 3 | 0.8 | 证据片段：'The a Black Start unit'。双重冠词的使用导致主语指代不明（是特指某个单元还是泛指），虽然可以推断为泛指，但形式上存在歧义。 | If a Black Start unit fails to meet the CAISO Black Start criteria specified in this procedure, the generator owner/operator shall submit a detailed explanation and a corrective action plan to the CAISO.
glm5 | R15 | C | Correctness | 2 | 0.9 | 证据片段：'The a Black Start unit'。原文存在明显的语法错误，违反了自然语言的正确性规则，属于低级书写错误。 | If a Black Start unit does not successfully pass the CAISO Black Start criteria specified in this procedure, the generator owner/operator shall provide an explanation and a plan to address the deficiency to the CAISO.
glm5 | R15 | V | Verifiable | 3 | 0.7 | 证据片段：'An explanation and a plan'。虽然可以验证是否提交了文档，但未规定解释的详细程度和计划的具体内容要求（如是否需要包含时间表），导致验证'合格性'的标准主观性较强。 | If a Black Start unit fails the CAISO Black Start criteria, the generator owner/operator shall submit a written explanation and a corrective action plan to the CAISO.
glm5 | R16 | U | Understandable | 4 | 0.9 | 需求使用了'periodicity'等学术词汇，整体句式较长，但语义基本清晰。证据片段：'The results of the testing and the justification for the periodicity of the testing'。 | 保持不变
glm5 | R16 | A | Unambiguous | 3 | 0.8 | 时间约束'within 30 days'置于括号内，未明确说明起止时间点，存在歧义。证据片段：'on request (within 30 days)'。虽然通常理解为收到请求后，但作为需求规范不够严谨。 | The results of the testing and the justification for the periodicity of the testing shall be provided to WECC or NERC within 30 days of receiving a request.
glm5 | R16 | C | Correctness | 4 | 0.6 | 假设上下文为NERC合规标准，需求逻辑正确，符合合规性报告的常规流程。证据片段：'shall be provided to WECC or NERC'。 | 保持不变
glm5 | R16 | V | Verifiable | 3 | 0.8 | 'justification'缺乏具体的验收标准，导致难以客观验证理由是否充分。证据片段：'justification for the periodicity of the testing'。 | The results of the testing and a documented justification for the periodicity of the testing shall be provided to WECC or NERC within 30 days of receiving a request.
glm5 | R17 | U | Understandable | 2 | 0.9 | 证据片段：'References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure...'。该文本仅为一系列名词短语的堆砌，缺乏标点符号、分隔符或列表结构，导致阅读困难，难以快速识别各个独立的引用文档。 | 使用项目符号或编号列表重新组织文档名称，并添加适当的标点符号。
glm5 | R17 | A | Unambiguous | 2 | 0.9 | 证据片段：'References'。该词作为需求描述的主体模糊不清，无法确定系统是需要'显示'这些引用、'符合'这些标准、还是'存储'这些文档名称，导致需求解释存在多种可能性。 | 将模糊的名词'References'替换为明确的系统行为动词，例如'系统应遵守'或'系统应提供以下文档的链接'。
glm5 | R17 | C | Correctness | 3 | 0.6 | 证据片段：'References ISO Tariff...'。虽然引用的文档名称可能属于领域内的正确术语，但需求条目本身语法结构不完整，缺乏主语和谓语，未能正确表达系统应实施的行为或应具备的属性。 | 将需求改写为完整的'主语+谓语+宾语'句式，确保需求描述的是系统的行为或约束。
glm5 | R17 | V | Verifiable | 1 | 1 | 证据片段：'References ISO Tariff...'。由于缺乏明确的动词（如'应显示'、'应遵守'），无法定义具体的测试步骤或通过标准，测试人员无法判断系统是否满足了该需求。 | 添加可验证的行为描述，例如'系统界面应包含以下参考文档列表'或'系统功能应符合以下标准要求'。

## issues_r0
rater | item | type | dimension | evidence | rewrite
qwen | R1 | U | Understandable | They must be able to self-start without any source of off-site electric power | Each designated black-start generator shall initiate its own startup sequence using only on-site energy sources (e.g., batteries, diesel starters, or flywheels), without connection to off-site AC power.
qwen | R1 | A | Unambiguous | maintain adequate voltage and frequency while energizing isolated transmission facilities and auxiliary loads of other generators | maintain terminal voltage within ±5% of 13.8 kV and system frequency within ±0.05 Hz for ≥300 seconds while energizing the 138-kV radial feeder segment between Bus A and Substation X and its own auxiliary loads (not those of other generators).
qwen | R1 | V | Verifiable | maintain adequate voltage and frequency while energizing isolated transmission facilities and auxiliary loads of other generators | Within 60 seconds of synchronization, the generator shall maintain voltage at 13.8 kV ±5% and frequency at 60.00 Hz ±0.05 Hz for ≥300 seconds while supplying a minimum load of 2.5 MW (comprising its own auxiliaries and the isolated 138-kV feeder).
kimi | R1 | A | Unambiguous | 'adequate voltage and frequency' | 电压稳态值保持在额定值±5 %以内，频率稳态值保持在50 Hz±0.2 Hz以内
kimi | R1 | V | Verifiable | 'maintain adequate voltage and frequency' | 在带孤立负载运行4 h期间，稳态电压偏差≤±5 %，稳态频率偏差≤±0.2 Hz，瞬态频率变化≤±1 Hz且恢复时间≤5 s
glm5 | R1 | A | Unambiguous | They | The [Target System Name/Generators]
glm5 | R1 | V | Verifiable | adequate voltage and frequency | voltage within [Min V] to [Max V] and frequency within [Min Hz] to [Max Hz]
qwen | R2 | U | Understandable | Such Test Dispatch Notice | The system shall generate a dispatch notice for black start tests.
qwen | R2 | A | Unambiguous | shall be marked “Black Start Test Notice.” | The dispatch notice PDF shall contain the exact visible text "Black Start Test Notice" centered in the top margin, in 16-point bold Arial font.
qwen | R2 | V | Verifiable | The Black Start Test shall be performed in accordance with the Ancillary Services Requirements Protocol in the CAISO Tariff. | Upon initiation of a black start test dispatch, the system shall output a file named BS_TEST_NOTICE_YYYYMMDD_HHMMSS.pdf containing the exact string "Black Start Test Notice" as the first non-whitespace line.
kimi | R2 | A | Unambiguous | in accordance with the Ancillary Services Requirements Protocol in the CAISO Tariff | in accordance with CAISO Tariff section 5.2.3 'Ancillary Services Requirements Protocol' (version 2024-03)
kimi | R2 | V | Verifiable | The Black Start Test shall be performed in accordance with... | The Black Start Test shall be executed following CAISO Tariff section 5.2.3; compliance shall be demonstrated by an independent audit report confirming 100% adherence to the protocol checklist.
glm5 | R2 | U | Understandable | Such Test Dispatch Notice | 测试调度通知
glm5 | R2 | A | Unambiguous | shall be marked | 系统应在测试调度通知的【通知类型】字段中显示“Black Start Test Notice”。
glm5 | R2 | V | Verifiable | performed in accordance with the Ancillary Services Requirements Protocol | 系统应依据《CAISO Tariff》中《Ancillary Services Requirements Protocol》第X章节执行黑启动测试流程。
qwen | R3 | U | Understandable | periods of constrained water availability | when the unit's primary reservoir elevation falls below 85% of its normal pool elevation, as reported hourly by USGS gauge ID 11425000
qwen | R3 | A | Unambiguous | constrained water availability | when either (a) the California Governor has declared a statewide drought emergency, or (b) the reservoir elevation for the unit's primary storage is ≤85% of normal pool elevation, per the latest hourly reading from USGS gauge ID 11425000
qwen | R3 | V | Verifiable | periods of constrained water availability | The CAISO shall not issue a Black Start Test request for a hydroelectric unit if, at the time of scheduling, both (i) the latest available reading from USGS gauge ID 11425000 shows reservoir elevation ≤85% of normal pool elevation, and (ii) the California Department of Water Resources has published an Active Drought Condition Alert for the watershed
kimi | R3 | A | Unambiguous | periods of constrained water availability | CAISO不得在水库水位≤EL. 120 m或收到水务调度'限水运行'指令期间，要求水电机组进行黑启动试验。
kimi | R3 | V | Verifiable | constrained water availability | CAISO不得在水库水位≤EL. 120 m或收到水务调度'限水运行'指令期间，要求水电机组进行黑启动试验。
glm5 | R3 | A | Unambiguous | periods of constrained water availability | The CAISO shall not request a Black Start Test for a hydroelectric Unit when the reservoir water level is below [Specific Threshold]% or when a drought emergency is declared by [Authority].
glm5 | R3 | V | Verifiable | periods of constrained water availability | The CAISO shall not request a Black Start Test for a hydroelectric Unit when the reservoir water level is below [Specific Threshold]% or when a drought emergency is declared by [Authority].
qwen | R4 | U | Understandable | Demonstrate at least every five years, through simulation or testing | The owner or operator shall execute a black start capability test or validated simulation at least once every 60 months.
qwen | R4 | A | Unambiguous | as required by the WECC BCP (if any) | as specified in the latest version of the WECC Black Start Capability Procedure (WECC BCP) published on or before the test date.
qwen | R4 | V | Verifiable | notify the CAISO RT Dispatcher by phone indicating the success or failure of the test | Within 24 hours of test completion, transmit BS-OK or BS-FAIL status code to CAISO RT Dispatcher via CAISO's Secure Messaging Portal (SMP) using Form CAISO-BS-NOTIFY-1.
kimi | R4 | A | Unambiguous | 'Demonstrate … that the unit can perform its intended functions' | The Owner shall demonstrate, at least once every five calendar years, that the unit can (a) energize a dead 230 kV bus within 15 minutes, (b) sustain 105 % rated voltage for 30 minutes, and (c) accept 25 % block load without frequency deviation exceeding 0.5 Hz, using either a field test or a CAISO-approved dynamic simulation model.
kimi | R4 | V | Verifiable | 'notify the CAISO RT Dispatcher by phone indicating the success or failure' | Within 24 hours of completing the Black Start test, the Owner shall (1) call the CAISO RT Dispatcher at +1-916-xxx-xxxx, record the call with date-time stamp, and (2) send a confirmation email to bstest@caiso.com containing the call recording and a pass/fail summary as defined in section X.
glm5 | R4 | A | Unambiguous | Submit any past reports for Black Start tests with the CAISO and WECC. | Submit all Black Start test reports generated within the last 5 years to the CAISO and WECC.
glm5 | R4 | A | Unambiguous | Those Participants who do not currently test their Black Start capability, will be required to test their Black Start capability. | Participants who have not conducted a Black Start test in the preceding 5 years shall conduct a test within 90 days of receiving Black Start generating unit status.
glm5 | R4 | C | Correctness | required by the WECC BCP (if any) and of this testing section. | required by the WECC BCP (if any) and the requirements of this testing section.
glm5 | R4 | V | Verifiable | Demonstrate... that the unit can perform its intended functions as required by the WECC BCP (if any)... | Demonstrate... that the unit meets the specific performance criteria (e.g., start-up time, load acceptance) defined in the WECC BCP and the CAISO Black Start Testing Guide.
qwen | R5 | A | Unambiguous | an indication of whether the tests met the requirements of this Black Start Testing section | Testing records shall include a Boolean field 'requirements_met' indicating whether all test cases executed under this section passed against their defined acceptance criteria.
qwen | R5 | V | Verifiable | an indication of whether the tests met the requirements of this Black Start Testing section | Testing records shall include a Boolean field 'requirements_met' indicating whether all test cases executed under this section passed against their defined acceptance criteria.
kimi | R5 | A | Unambiguous | an indication of whether the tests met the requirements | a Boolean field “testPassed” with value true if all applicable Black Start Test cases defined in Section X.Y pass, otherwise false
kimi | R5 | V | Verifiable | an indication of whether the tests met the requirements | a Boolean field “testPassed” with value true if all applicable Black Start Test cases defined in Section X.Y pass, otherwise false
glm5 | R5 | A | Unambiguous | dates of the tests | start date and time of each test
glm5 | R5 | A | Unambiguous | an indication of whether the tests met the requirements | a test result status of 'Pass' or 'Fail'
glm5 | R5 | V | Verifiable | duration of the tests | duration of each test in minutes
qwen | R6 | U | Understandable | emergency voltage limits | voltage limits specified in NERC BAL-003-3 Section 4.2.1 (±10% of nominal voltage at the unit's high-side bus)
qwen | R6 | A | Unambiguous | in accordance with NERC reliability standards | in accordance with NERC BAL-003-3 (Effective Date: 2023-07-01) Section 4.2.1 and TOP-004-3 Section 5.3.2
qwen | R6 | V | Verifiable | must have the ability to maintain voltage within emergency voltage limits over a range of loading from no external load to full external load | The Black Start unit shall maintain voltage at its high-side bus within ±10% of nominal voltage for ≥30 seconds under each of the following steady-state loading conditions: (a) 0.0 MW ± 0.1 MW, (b) 50% of rated nameplate capacity ± 1%, and (c) 100% of rated nameplate capacity ± 1%, measured using Class 0.2 instrumentation per IEEE C57.13.
kimi | R6 | A | Unambiguous | emergency voltage limits | The Black Start unit shall maintain its output voltage between 0.95 pu and 1.05 pu while supplying active power from 0 % to 100 % of its nameplate rating, as defined in NERC PRC-024-2 clause 4.3.
kimi | R6 | V | Verifiable | maintain voltage within emergency voltage limits over a range of loading from no external load to full external load | During factory acceptance test, the Black Start unit shall be stepped from 0 % to 25 %, 50 %, 75 % and 100 % of nameplate active power; voltage shall remain within 0.95–1.05 pu for ≥5 min at each step with maximum 2 % overshoot and recovery time ≤2 s.
glm5 | R6 | A | Unambiguous | in accordance with NERC reliability standards | in accordance with NERC PRC-024-2 (or other specific standard ID)
glm5 | R6 | V | Verifiable | emergency voltage limits | voltage limits of [Min Voltage] to [Max Voltage]
glm5 | R6 | V | Verifiable | range of loading from no external load to full external load | loading levels of 0%, 50%, and 100% of rated capacity
qwen | R7 | U | Understandable | capable of operating in an isochronous mode | The Black Start unit's governor shall maintain system frequency within ±0.02 Hz of 50 Hz (or 60 Hz, per site specification) when operating in islanded mode with no external grid reference and under load steps from 0% to 100% rated output.
qwen | R7 | A | Unambiguous | capable of operating in an isochronous mode | The governor shall be pre-configured and locked in isochronous control mode prior to black start initiation, and shall remain in that mode throughout the black start sequence until grid synchronization.
qwen | R7 | V | Verifiable | capable of operating in an isochronous mode | During factory acceptance test (FAT), the governor shall demonstrate frequency regulation within ±0.02 Hz of nominal (50/60 Hz) for three consecutive 20% load steps (0→20→40→60%) in islanded mode, measured using calibrated PMU; deviation exceeding ±0.05 Hz at any 100-ms interval shall constitute failure.
kimi | R7 | A | Unambiguous | The Black Start unit must be equipped with governors that are capable of operating in an isochronous mode | 每台黑启动机组的调速系统应在孤岛运行时，能在额定频率50 Hz±0.1 Hz范围内以等时模式连续运行≥30 min
kimi | R7 | V | Verifiable | capable of operating in an isochronous mode | 验收测试：断开外网，机组带厂用负荷30%Pn，频率保持50 Hz±0.1 Hz持续30 min，记录频率超调≤0.05 Hz
glm5 | R7 | C | Correctness | must be equipped | The Black Start unit shall be equipped with governors that are capable of operating in an isochronous mode.
glm5 | R7 | V | Verifiable | capable of operating in an isochronous mode | The Black Start unit shall be equipped with governors capable of isochronous operation, maintaining a steady-state frequency deviation within ±[X] Hz under [Y]% load steps.
qwen | R8 | U | Understandable | Adequate transmission capacity | Transmission capacity rated ≥ 25 MVA at 34.5 kV
qwen | R8 | A | Unambiguous | the source providing station services to other specified generating stations | Substation SS-BS01, Bus B2, as identified in Appendix A
qwen | R8 | V | Verifiable | shall be available | Shall be demonstrated via IEEE 30-bus load flow simulation showing ≤ 5% voltage drop and ≥ 1.2 pu short-circuit ratio at the interconnection point under N-1 contingency, verified by Test Report TR-BS08
kimi | R8 | A | Unambiguous | Adequate transmission capacity | The transmission path shall provide ≥150 MVA continuous transfer capability at 220 kV.
kimi | R8 | A | Unambiguous | other specified generating stations | A站、B站、C站（详见附录A清单）。
kimi | R8 | V | Verifiable | Adequate transmission capacity shall be available | Verification: During the annual black-start test, record 15-minute average power flow ≥150 MVA for 2 consecutive hours with no equipment overload alarm.
glm5 | R8 | A | Unambiguous | Adequate transmission capacity | The transmission capacity shall be no less than [Value] MW.
glm5 | R8 | A | Unambiguous | specified generating stations | generating stations listed in [Reference Document ID]
glm5 | R8 | V | Verifiable | shall be available | The transmission path shall be operational and capable of carrying the required load within [Timeframe] of a request.
qwen | R9 | U | Understandable | applicable transmission path | the 230 kV transmission path between Substation Alpha and Bus Gamma, as defined in System Architecture Document v2.1, Section 4.3
qwen | R9 | A | Unambiguous | without assistance from the electrical system | using only on-site, non-grid-dependent energy sources (i.e., dedicated black start diesel generator and/or battery bank supplying control and prime mover power), and with zero reliance on AC voltage or current sourced from the bulk electric system
qwen | R9 | V | Verifiable | must be capable of starting and energizing the applicable transmission path without assistance from the electrical system | Within 120 seconds of initiation, the Black Start unit shall establish and maintain ≥ 0.95 p.u. voltage and 59.95–60.05 Hz frequency at the receiving end of the 230 kV transmission path between Substation Alpha and Bus Gamma, measured per IEEE 1159 Class A power quality monitoring.
kimi | R9 | A | Unambiguous | applicable transmission path | the 230 kV Main Export Line between Black Start Unit and Grid Substation A
kimi | R9 | V | Verifiable | without assistance from the electrical system | with zero external electrical energy input during the start-up and line energization process
glm5 | R9 | A | Unambiguous | applicable transmission path | the transmission path defined in [System_Configuration_Data]
glm5 | R9 | A | Unambiguous | without assistance | while isolated from the external electrical grid
glm5 | R9 | V | Verifiable | must be capable of | shall start and energize
qwen | R10 | U | Understandable | • Hot, steam-driven turbines, within 2.5 hours of the initiation of the Black Start process. | steam-driven turbine units operating in hot standby mode: 2.5 hours
qwen | R10 | A | Unambiguous | Hot, steam-driven turbines | steam-driven turbine units operating in hot standby mode
qwen | R10 | V | Verifiable | within 2.5 hours of the initiation of the Black Start process | measured from the timestamp of the official Black Start initiation command (issued by the Reliability Coordinator) to the timestamp of verified, stable grid synchronization (defined as sustained 60 Hz frequency ±0.05 Hz and voltage within ±5% of nominal for ≥30 seconds)
kimi | R10 | U | Understandable | start-up/synchronizing time limits | Hydroelectric generating units shall complete startup within 30 minutes after the dispatcher issues the Black Start command.
kimi | R10 | A | Unambiguous | specific start time limits are negotiated | If the certified Black Start unit uses technology not listed above, its startup completion time shall be documented in the test plan and shall not exceed 4 hours.
kimi | R10 | V | Verifiable | specific start time limits are negotiated | The negotiated startup completion time shall be recorded as a numeric value (minutes) in the test plan and used as the pass/fail criterion.
glm5 | R10 | A | Unambiguous | start-up/synchronizing time limits | start-up to synchronizing time limits
glm5 | R10 | A | Unambiguous | Hot, steam-driven turbines | Steam-driven turbines in a Hot state (defined as: turbine metal temperature within 50°C of rated temperature, or downtime less than 48 hours)
glm5 | R10 | V | Verifiable | specific start time limits are negotiated | specific start time limits shall be documented in the Black Start Service Agreement prior to the testing phase
qwen | R11 | U | Understandable | All Black Start Generating Units | Each generating unit formally designated as a Black Start Generating Unit in the CAISO Resource Adequacy Database
qwen | R11 | A | Unambiguous | technical requirements specified by the CAISO | all mandatory technical criteria in CAISO Tariff Appendix D, Revision 4.2 (effective 2023-09-15), Sections D.1 through D.5
qwen | R11 | V | Verifiable | must satisfy technical requirements specified by the CAISO | shall provide a valid CAISO Black Start Certification Letter issued within the prior 12 months, verifiable by the System Operator during unit registration
kimi | R11 | A | Unambiguous | 'technical requirements specified by the CAISO' | 机组须满足CAISO Technical Bulletin 2023-01《Black Start Unit Certification Criteria》第4-7节所列全部技术要求。
kimi | R11 | V | Verifiable | 'must satisfy technical requirements' | 机组应在型式试验中于30分钟内完成黑启动并建立≥5%额定电压，试验报告须由CAISO认可的第三方出具。
glm5 | R11 | A | Unambiguous | technical requirements specified by the CAISO | All Black Start Generating Units must satisfy the technical requirements specified in 'CAISO Business Practice Manual: Reliability Standards', Version [X], Section [Y].
glm5 | R11 | V | Verifiable | satisfy technical requirements | All Black Start Generating Units must satisfy the technical requirements specified in 'CAISO Business Practice Manual: Reliability Standards', Version [X], Section [Y].
qwen | R12 | U | Understandable | from time to time | shall execute performance tests at least once per calendar quarter
qwen | R12 | A | Unambiguous | with or without prior notification | shall provide written notification at least 48 hours prior to scheduled performance tests; unscheduled tests require documented justification referencing CAISO Grid Emergency Declaration criteria
qwen | R12 | V | Verifiable | shall from time to time undertake performance tests, with or without prior notification | shall execute, record, and archive results of each performance test including test date, scope, configuration, input data version, and pass/fail determination against acceptance criteria defined in Appendix B
kimi | R12 | A | Unambiguous | with or without prior notification | CAISO may conduct performance tests either (a) with no less than 10 business days prior written notice, or (b) without notice when required for emergency reliability assessment.
kimi | R12 | V | Verifiable | from time to time undertake performance tests | CAISO shall execute performance tests at least once per calendar quarter, covering ≥ 80 % of critical-path transactions and achieving ≤ 2 second 95th-percentile response time.
glm5 | R12 | A | Unambiguous | from time to time | The CAISO shall undertake performance tests at least once per calendar year, with or without prior notification.
glm5 | R12 | V | Verifiable | from time to time | The CAISO shall undertake performance tests at least once per calendar year, with or without prior notification.
qwen | R13 | U | Understandable | respond to conditions on the CAISO Controlled Grid | respond to one or more of the following verified grid conditions: (a) system frequency falling below 59.3 Hz for ≥15 seconds; (b) loss of ≥300 MW of synchronous generation within a single balancing authority area; or (c) confirmed islanding of the CAISO-controlled grid from the Western Interconnection.
qwen | R13 | A | Unambiguous | shall have the sole right to determine when the operation... is required | CAISO shall issue a Black Start Activation Directive within 120 seconds of confirming any condition listed in U13.1; the determination of whether such a condition exists shall be based solely on real-time telemetry validated per CAISO Telemetry Validation Procedure v4.2.
qwen | R13 | V | Verifiable | shall have the sole right to determine when the operation of Black Start Generating Unit is required | Within 120 seconds of confirming a condition in U13.1, CAISO shall broadcast a Black Start Activation Directive via the CAISO Real-Time Messaging System (RTMS), logged with timestamp, directive ID, and triggering condition code — observable in the CAISO Operational Log Archive.
kimi | R13 | A | Unambiguous | conditions on the CAISO Controlled Grid | CAISO shall have the sole authority to initiate Black Start Generating Unit operation upon detection of a total blackout or frequency below 59.0 Hz on the CAISO Controlled Grid.
kimi | R13 | V | Verifiable | determine when the operation...is required | CAISO shall document in the Black Start Event Log the timestamp, measured grid condition values, and decision rationale each time it initiates Black Start Generating Unit operation.
glm5 | R13 | A | Unambiguous | sole right to determine | The System shall restrict the initiation of Black Start Generating Unit operations to CAISO authorized users.
glm5 | R13 | V | Verifiable | determine when the operation... is required | The System shall provide a control interface for CAISO authorized users to trigger the Black Start Generating Unit operation.
qwen | R14 | U | Understandable | Each of he four points must reside in a different hour of the test | Each of the four test points must be executed in a distinct 60-minute interval, measured from test start time T₀.
qwen | R14 | A | Unambiguous | a different hour of the test | Each of the four test points must be executed in a distinct 60-minute interval, where interval i spans [T₀ + (i−1)×3600 s, T₀ + i×3600 s), for i ∈ {1,2,3,4}.
qwen | R14 | V | Verifiable | must reside in a different hour of the test | The system shall log the execution timestamp of each test point; analysis of logs shall confirm exactly one test point executed in each of four non-overlapping 3600-second intervals starting at test initiation.
kimi | R14 | U | Understandable | Each of he four points must reside in a different hour of the test. | The four measurement events shall each occur within a distinct 60-minute interval of the 4-hour test run.
kimi | R14 | A | Unambiguous | points | measurement events
kimi | R14 | C | Correctness | he four points | the four measurement events
kimi | R14 | V | Verifiable | reside in a different hour of the test | be timestamped and fall within a unique 60-minute interval (00:00–59:59, 01:00–01:59, 02:00–02:59, 03:00–03:59) of the test run; no two timestamps shall share the same interval
glm5 | R14 | U | Understandable | Each of he four points | Each of the four data points must reside in a different hour of the test.
glm5 | R14 | A | Unambiguous | four points ... different hour | Each of the four data points shall have a timestamp falling within a unique clock hour (e.g., HH:00 to HH:59) during the test execution.
glm5 | R14 | C | Correctness | Each of he | Each of the four points must reside in a different hour of the test.
glm5 | R14 | V | Verifiable | reside in a different hour | The timestamps of the four data points shall fall into four distinct clock hours during the test execution.
qwen | R15 | U | Understandable | The a Black Start unit did not successfully pass the CAISO Black Start criteria specified in this procedure | If a Black Start unit fails to satisfy any mandatory item in Table 3.2 (Black Start Readiness Criteria), then the generator owner/operator shall submit a corrective action report to CAISO within 5 business days.
qwen | R15 | A | Unambiguous | CAISO Black Start criteria specified in this procedure | any mandatory item listed in Table 3.2 (Black Start Readiness Criteria, Rev. 2024-09)
qwen | R15 | V | Verifiable | An explanation and a plan to address and correct the deficiency shall be provided to the CAISO by the generator owner/operator | The corrective action report shall include: (a) root cause analysis using the 5-Whys method; (b) corrective actions with assigned owners and due dates; (c) evidence of implementation for at least one action prior to submission; and (d) submission in PDF/A-1b format to CAISO via the Secure Portal before 17:00 PT on the fifth business day following notification of non-compliance.
kimi | R15 | A | Unambiguous | “If… Then… The a Black Start unit did not successfully pass…” | If a Black Start unit fails any CAISO Black Start criterion listed in Section 4.2, then…
kimi | R15 | V | Verifiable | “An explanation and a plan to address and correct the deficiency shall be provided…” | The generator owner/operator shall submit to CAISO within 10 business days a written deficiency report and a corrective-action plan that lists each failed criterion, root cause, and scheduled completion date.
glm5 | R15 | U | Understandable | If… Then… The a Black Start unit | If a Black Start unit fails to pass the CAISO Black Start criteria specified in this procedure, the generator owner/operator shall provide an explanation and a corrective plan to the CAISO.
glm5 | R15 | C | Correctness | The a Black Start unit | If a Black Start unit does not successfully pass the CAISO Black Start criteria specified in this procedure, the generator owner/operator shall provide an explanation and a plan to address the deficiency to the CAISO.
glm5 | R15 | V | Verifiable | An explanation and a plan | If a Black Start unit fails the CAISO Black Start criteria, the generator owner/operator shall submit a written explanation and a corrective action plan to the CAISO.
qwen | R16 | U | Understandable | The results of the testing and the justification for the periodicity of the testing | The system shall provide, upon request, (1) all raw test execution logs and (2) a dated, signed statement justifying the selected testing interval (e.g., 90 days).
qwen | R16 | A | Unambiguous | WECC or NERC on request | WECC or NERC (inclusive), acting through an authorized representative, upon receipt of a written request signed by that representative.
qwen | R16 | V | Verifiable | shall be provided to WECC or NERC on request (within 30 days) | Within 30 calendar days of receipt of a written request from an authorized representative of WECC or NERC, the system shall deliver via secure web portal a ZIP archive containing: (a) all raw test execution logs (in UTF-8 plain text), (b) a PDF report summarizing test outcomes and pass/fail status per test case ID, and (c) a signed statement justifying the selected testing interval with reference to §X.Y of the applicable compliance standard.
kimi | R16 | A | Unambiguous | testing | 每年度执行的内部网络安全渗透测试
kimi | R16 | A | Unambiguous | justification for the periodicity of the testing | 包含风险评估矩阵与测试频率映射表的备忘录
kimi | R16 | C | Correctness | provided to WECC or NERC on request (within 30 days) | 通过 WECC 安全门户上传，且上传完成日期不晚于请求送达后的第 30 个自然日
kimi | R16 | V | Verifiable | justification for the periodicity | 备忘录须说明年度风险等级≥High 的资产比例>5% 时测试频率为年度，否则为每 18 个月
glm5 | R16 | A | Unambiguous | on request (within 30 days) | within 30 days of receiving a request
glm5 | R16 | V | Verifiable | justification for the periodicity of the testing | a documented justification for the periodicity of the testing
qwen | R17 | U | Understandable | References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203, Reliability Must Run Unit Commitment and Dispatch... | 系统应确保所有黑启动发电单元的认证测试活动符合ISO Tariff Section 8.3.3、CAISO G-203、CAISO G-213、CAISO G-213H及CAISO G-213I的最新有效版本要求；
qwen | R17 | A | Unambiguous | NERC Reliability Standard EOP-005 System Restoration Plans EOP-009 Documentation of Blackstart Generating Unit Test Results | 系统生成的黑启动测试报告必须包含EOP-009第4.2条规定的全部7个必填字段，并采用CAISO G-213H指定的PDF模板格式；
qwen | R17 | V | Verifiable | References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203, Reliability Must Run Unit Commitment and Dispatch... | 系统应在用户提交黑启动测试报告后自动校验：① 文件名符合'BSR-{UnitID}-{YYYYMMDD}-vN.pdf'格式；② 元数据中包含EOP-009要求的TestDate、FuelType、StartSuccessRate字段且非空；③ 签章页含CAISO授权签字人数字签名。
kimi | R17 | U | Understandable | References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203... | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供对应合格报告。
kimi | R17 | A | Unambiguous | References ISO Tariff Section 8.3.3... | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供对应合格报告。
kimi | R17 | V | Verifiable | References ISO Tariff Section 8.3.3... | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供由 CAISO 签署的合格测试报告；验收测试将核查报告存在性及结论为'通过'。
glm5 | R17 | U | Understandable | References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203... | 系统应遵守以下标准与规程： 1. ISO Tariff Section 8.3.3 Certification and Testing Requirements； 2. CAISO Operating Procedure G-203 Reliability Must Run Unit Commitment and Dispatch； 3. CAISO Operating Procedure G-213 Generator Certification Testing； 4. CAISO Operating Procedure G-213H Black Start Test Report Form； 5. CAISO Operating Procedure G-213I Black Start Process Flowchart； 6. NERC Reliability Standard EOP-005 System Restoration Plans； 7. EOP-009 Documentation of Blackstart Generating Unit Test Results。
glm5 | R17 | A | Unambiguous | References | 系统应遵守以下标准与规程...
glm5 | R17 | V | Verifiable | References ISO Tariff Section 8.3.3... | 系统应遵守以下标准与规程...（验证方法：检查系统设计文档或功能实现是否符合所列标准的具体条款）。

## issues_r1
rater | item | type | dimension | evidence | rewrite
qwen | R12 | V | Verifiable | from time to time | at least once per calendar quarter
qwen | R13 | A | Unambiguous | determine when the operation of Black Start Generating Unit is required to respond to conditions on the CAISO Controlled Grid | initiate Black Start Generating Unit operation within 120 seconds of confirming any of the following grid conditions: (a) system islanding detected via loss of >95% of tie-line power flows for ≥5 seconds; (b) frequency falling below 59.3 Hz for ≥10 seconds
qwen | R13 | V | Verifiable | shall have the sole right to determine when the operation of Black Start Generating Unit is required | Within 120 seconds of confirming a condition in U13.1, CAISO shall broadcast a Black Start Activation Directive via the CAISO Real-Time Messaging System (RTMS), logged with timestamp, directive ID, and triggering grid condition values in the Black Start Event Log.
qwen | R17 | U | Understandable | References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203, Reliability Must Run Unit Commitment and Dispatch CAISO Operating Procedure G-213 Generator Certification Testing CAISO Operating Procedure G-213H Black Start Test Report Form CAISO Operating Procedure G-213I Black Start Process Flowchart NERC Reliability Standard EOP-005 System Restoration Plans EOP-009 Documentation of Blackstart Generating Unit Test Results | The system shall comply with and generate documentation satisfying: (1) ISO Tariff Section 8.3.3 Certification and Testing Requirements; (2) CAISO G-203 §8.3.3; (3) CAISO G-213 §4.1–4.5; (4) CAISO G-213H Appendix A (PDF template); (5) CAISO G-213I §2.1–2.4 (process flow); (6) NERC EOP-005 §3.2 (restoration plan integration); and (7) NERC EOP-009 §4.2 (seven mandatory test result fields).
qwen | R17 | A | Unambiguous | References | shall comply with and generate documentation satisfying
qwen | R17 | V | Verifiable | References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203, Reliability Must Run Unit Commitment and Dispatch... | The system shall generate a black start test report PDF conforming to CAISO G-213H Appendix A, containing all seven EOP-009 §4.2 mandatory fields (TestDate, FuelType, StartSuccessRate, etc.) with non-empty values, and bearing a valid CAISO-authorized digital signature verified at runtime.
qwen | R2 | U | Understandable | Such Test Dispatch Notice | The Black Start Test Dispatch Notice generated by the system
qwen | R2 | A | Unambiguous | shall be marked “Black Start Test Notice.” | The dispatch notice PDF shall contain the exact visible text "Black Start Test Notice" centered in the top margin, in 16-point bold Arial font.
qwen | R2 | A | Unambiguous | in accordance with the Ancillary Services Requirements Protocol in the CAISO Tariff | in accordance with CAISO Tariff section 5.2.3 'Ancillary Services Requirements Protocol' (version 2024-03)
qwen | R2 | V | Verifiable | The Black Start Test shall be performed in accordance with the Ancillary Services Requirements Protocol in the CAISO Tariff. | Upon initiation of a black start test dispatch, the system shall output a file named BS_TEST_NOTICE_YYYYMMDD_HHMMSS.pdf containing the exact string 'Black Start Test Notice' as the first non-whitespace text in the document, rendered in 16-point bold Arial font, and shall log the file generation timestamp and SHA-256 hash in the Audit Trail.
qwen | R6 | A | Unambiguous | in accordance with NERC reliability standards | in accordance with NERC BAL-003-3 Section 4.2.1 (Effective Date: 2023-07-01) and TOP-004-3 Section 5.3.2
qwen | R6 | A | Unambiguous | emergency voltage limits | ±10% of nominal voltage at the high-side bus, per NERC BAL-003-3 Section 4.2.1
qwen | R6 | V | Verifiable | maintain voltage within emergency voltage limits over a range of loading from no external load to full external load | maintain voltage at its high-side bus within ±10% of nominal voltage for ≥30 seconds under each of the following steady-state loading conditions: (a) 0.0 MW ± 0.1 MW, (b) 50 MW ± 0.1 MW, (c) 100% of rated active power
qwen | R9 | A | Unambiguous | applicable transmission path | the 230 kV Main Export Line between Black Start Unit and Grid Substation A
qwen | R9 | A | Unambiguous | without assistance from the electrical system | using only on-site, non-grid-dependent energy sources (i.e., dedicated black start diesel generator and/or battery bank supplying control and prime mover power), with zero AC voltage or power input from the external electrical grid
qwen | R1 | U | Understandable | They must be able to self-start without any source of off-site electric power | Each designated black-start generator shall initiate its own startup sequence using only on-site energy sources (e.g., batteries, diesel starters, or flywheels), without connection to off-site AC power.
qwen | R1 | A | Unambiguous | maintain adequate voltage and frequency while energizing isolated transmission facilities and auxiliary loads of other generators | maintain terminal voltage within ±5% of 13.8 kV and system frequency within ±0.05 Hz for ≥300 seconds while energizing the 138-kV radial feeder segment between Bus A and Substation X and its own auxiliary loads (not those of other generators).
qwen | R1 | V | Verifiable | maintain adequate voltage and frequency while energizing isolated transmission facilities and auxiliary loads of other generators | Within 60 seconds of synchronization, the generator shall maintain voltage at 13.8 kV ±5% and frequency at 60.00 Hz ±0.05 Hz for ≥300 seconds while supplying a minimum load of 2.5 MW (comprising its own auxiliaries and the isolated 138-kV feeder).
qwen | R3 | U | Understandable | periods of constrained water availability | when the unit's primary reservoir elevation falls below 85% of its normal pool elevation, as reported hourly by USGS gauge ID 11425000
qwen | R3 | A | Unambiguous | constrained water availability | when either (a) the California Governor has declared a statewide drought emergency, or (b) the reservoir elevation for the unit's primary storage is ≤85% of normal pool elevation, per the latest hourly reading from USGS gauge ID 11425000
qwen | R3 | V | Verifiable | periods of constrained water availability | The CAISO shall not issue a Black Start Test request for a hydroelectric unit if, at the time of scheduling, both (i) the latest available reading from USGS gauge ID 11425000 shows reservoir elevation ≤85% of normal pool elevation, and (ii) the California Department of Water Resources has published an Active Drought Condition Alert for the watershed
qwen | R4 | U | Understandable | Demonstrate at least every five years, through simulation or testing | The owner or operator shall execute a black start capability test or validated simulation at least once every 60 months.
qwen | R4 | A | Unambiguous | as required by the WECC BCP (if any) | as specified in the latest version of the WECC Black Start Capability Procedure (WECC BCP) published on or before the test date.
qwen | R4 | V | Verifiable | notify the CAISO RT Dispatcher by phone indicating the success or failure of the test | Within 24 hours of test completion, transmit BS-OK or BS-FAIL status code to CAISO RT Dispatcher via CAISO's Secure Messaging Portal (SMP) using Form CAISO-BS-NOTIFY-1.
qwen | R5 | A | Unambiguous | an indication of whether the tests met the requirements of this Black Start Testing section | Testing records shall include a Boolean field 'requirements_met' indicating whether all test cases executed under this section passed against their defined acceptance criteria.
qwen | R5 | V | Verifiable | an indication of whether the tests met the requirements of this Black Start Testing section | Testing records shall include a Boolean field 'requirements_met' indicating whether all test cases executed under this section passed against their defined acceptance criteria.
qwen | R7 | U | Understandable | capable of operating in an isochronous mode | The Black Start unit's governor shall maintain system frequency within ±0.02 Hz of 50 Hz (or 60 Hz, per site specification) when operating in islanded mode with no external grid reference and under load steps from 0% to 100% rated output.
qwen | R7 | A | Unambiguous | capable of operating in an isochronous mode | The governor shall be pre-configured and locked in isochronous control mode prior to black start initiation, and shall remain in that mode throughout the black start sequence until grid synchronization.
qwen | R7 | V | Verifiable | capable of operating in an isochronous mode | During factory acceptance test (FAT), the governor shall demonstrate frequency regulation within ±0.02 Hz of nominal (50/60 Hz) for three consecutive 20% load steps (0→20→40→60%) in islanded mode, measured using calibrated PMU; deviation exceeding ±0.05 Hz at any 100-ms interval shall constitute failure.
qwen | R8 | U | Understandable | Adequate transmission capacity | Transmission capacity rated ≥ 25 MVA at 34.5 kV
qwen | R8 | A | Unambiguous | the source providing station services to other specified generating stations | Substation SS-BS01, Bus B2, as identified in Appendix A
qwen | R8 | V | Verifiable | shall be available | Shall be demonstrated via IEEE 30-bus load flow simulation showing ≤ 5% voltage drop and ≥ 1.2 pu short-circuit ratio at the interconnection point under N-1 contingency, verified by Test Report TR-BS08
qwen | R10 | U | Understandable | • Hot, steam-driven turbines, within 2.5 hours of the initiation of the Black Start process. | steam-driven turbine units operating in hot standby mode: 2.5 hours
qwen | R10 | A | Unambiguous | Hot, steam-driven turbines | steam-driven turbine units operating in hot standby mode
qwen | R10 | V | Verifiable | within 2.5 hours of the initiation of the Black Start process | measured from the timestamp of the official Black Start initiation command (issued by the Reliability Coordinator) to the timestamp of verified, stable grid synchronization (defined as sustained 60 Hz frequency ±0.05 Hz and voltage within ±5% of nominal for ≥30 seconds)
qwen | R11 | U | Understandable | All Black Start Generating Units | Each generating unit formally designated as a Black Start Generating Unit in the CAISO Resource Adequacy Database
qwen | R11 | A | Unambiguous | technical requirements specified by the CAISO | all mandatory technical criteria in CAISO Tariff Appendix D, Revision 4.2 (effective 2023-09-15), Sections D.1 through D.5
qwen | R11 | V | Verifiable | must satisfy technical requirements specified by the CAISO | shall provide a valid CAISO Black Start Certification Letter issued within the prior 12 months, verifiable by the System Operator during unit registration
qwen | R14 | U | Understandable | Each of he four points must reside in a different hour of the test | Each of the four test points must be executed in a distinct 60-minute interval, measured from test start time T₀.
qwen | R14 | A | Unambiguous | a different hour of the test | Each of the four test points must be executed in a distinct 60-minute interval, where interval i spans [T₀ + (i−1)×3600 s, T₀ + i×3600 s), for i ∈ {1,2,3,4}.
qwen | R14 | V | Verifiable | must reside in a different hour of the test | The system shall log the execution timestamp of each test point; analysis of logs shall confirm exactly one test point executed in each of four non-overlapping 3600-second intervals starting at test initiation.
qwen | R15 | U | Understandable | The a Black Start unit did not successfully pass the CAISO Black Start criteria specified in this procedure | If a Black Start unit fails to satisfy any mandatory item in Table 3.2 (Black Start Readiness Criteria), then the generator owner/operator shall submit a corrective action report to CAISO within 5 business days.
qwen | R15 | A | Unambiguous | CAISO Black Start criteria specified in this procedure | any mandatory item listed in Table 3.2 (Black Start Readiness Criteria, Rev. 2024-09)
qwen | R15 | V | Verifiable | An explanation and a plan to address and correct the deficiency shall be provided to the CAISO by the generator owner/operator | The corrective action report shall include: (a) root cause analysis using the 5-Whys method; (b) corrective actions with assigned owners and due dates; (c) evidence of implementation for at least one action prior to submission; and (d) submission in PDF/A-1b format to CAISO via the Secure Portal before 17:00 PT on the fifth business day following notification of non-compliance.
qwen | R16 | U | Understandable | The results of the testing and the justification for the periodicity of the testing | The system shall provide, upon request, (1) all raw test execution logs and (2) a dated, signed statement justifying the selected testing interval (e.g., 90 days).
qwen | R16 | A | Unambiguous | WECC or NERC on request | WECC or NERC (inclusive), acting through an authorized representative, upon receipt of a written request signed by that representative.
qwen | R16 | V | Verifiable | shall be provided to WECC or NERC on request (within 30 days) | Within 30 calendar days of receipt of a written request from an authorized representative of WECC or NERC, the system shall deliver via secure web portal a ZIP archive containing: (a) all raw test execution logs (in UTF-8 plain text), (b) a PDF report summarizing test outcomes and pass/fail status per test case ID, and (c) a signed statement justifying the selected testing interval with reference to §X.Y of the applicable compliance standard.
kimi | R1 | A | Unambiguous | 'adequate voltage and frequency' | 电压稳态值保持在额定值±5 %以内，频率稳态值保持在50 Hz±0.2 Hz以内
kimi | R1 | V | Verifiable | 'maintain adequate voltage and frequency' | 在带孤立负载运行4 h期间，稳态电压偏差≤±5 %，稳态频率偏差≤±0.2 Hz，瞬态频率变化≤±1 Hz且恢复时间≤5 s
kimi | R2 | A | Unambiguous | in accordance with the Ancillary Services Requirements Protocol in the CAISO Tariff | in accordance with CAISO Tariff section 5.2.3 'Ancillary Services Requirements Protocol' (version 2024-03)
kimi | R2 | V | Verifiable | The Black Start Test shall be performed in accordance with... | The Black Start Test shall be executed following CAISO Tariff section 5.2.3; compliance shall be demonstrated by an independent audit report confirming 100% adherence to the protocol checklist.
kimi | R3 | A | Unambiguous | periods of constrained water availability | CAISO不得在水库水位≤EL. 120 m或收到水务调度'限水运行'指令期间，要求水电机组进行黑启动试验。
kimi | R3 | V | Verifiable | constrained water availability | CAISO不得在水库水位≤EL. 120 m或收到水务调度'限水运行'指令期间，要求水电机组进行黑启动试验。
kimi | R4 | A | Unambiguous | 'Demonstrate … that the unit can perform its intended functions' | The Owner shall demonstrate, at least once every five calendar years, that the unit can (a) energize a dead 230 kV bus within 15 minutes, (b) sustain 105 % rated voltage for 30 minutes, and (c) accept 25 % block load without frequency deviation exceeding 0.5 Hz, using either a field test or a CAISO-approved dynamic simulation model.
kimi | R4 | V | Verifiable | 'notify the CAISO RT Dispatcher by phone indicating the success or failure' | Within 24 hours of completing the Black Start test, the Owner shall (1) call the CAISO RT Dispatcher at +1-916-xxx-xxxx, record the call with date-time stamp, and (2) send a confirmation email to bstest@caiso.com containing the call recording and a pass/fail summary as defined in section X.
kimi | R5 | A | Unambiguous | an indication of whether the tests met the requirements | a Boolean field “testPassed” with value true if all applicable Black Start Test cases defined in Section X.Y pass, otherwise false
kimi | R5 | V | Verifiable | an indication of whether the tests met the requirements | a Boolean field “testPassed” with value true if all applicable Black Start Test cases defined in Section X.Y pass, otherwise false
kimi | R6 | A | Unambiguous | emergency voltage limits | The Black Start unit shall maintain its output voltage between 0.95 pu and 1.05 pu while supplying active power from 0 % to 100 % of its nameplate rating, as defined in NERC PRC-024-2 clause 4.3.
kimi | R6 | V | Verifiable | maintain voltage within emergency voltage limits over a range of loading from no external load to full external load | During factory acceptance test, the Black Start unit shall be stepped from 0 % to 25 %, 50 %, 75 % and 100 % of nameplate active power; voltage shall remain within 0.95–1.05 pu for ≥5 min at each step with maximum 2 % overshoot and recovery time ≤2 s.
kimi | R7 | A | Unambiguous | The Black Start unit must be equipped with governors that are capable of operating in an isochronous mode | 每台黑启动机组的调速系统应在孤岛运行时，能在额定频率50 Hz±0.1 Hz范围内以等时模式连续运行≥30 min
kimi | R7 | V | Verifiable | capable of operating in an isochronous mode | 验收测试：断开外网，机组带厂用负荷30%Pn，频率保持50 Hz±0.1 Hz持续30 min，记录频率超调≤0.05 Hz
kimi | R8 | A | Unambiguous | Adequate transmission capacity | The transmission path shall provide ≥150 MVA continuous transfer capability at 220 kV.
kimi | R8 | A | Unambiguous | other specified generating stations | A站、B站、C站（详见附录A清单）。
kimi | R8 | V | Verifiable | Adequate transmission capacity shall be available | Verification: During the annual black-start test, record 15-minute average power flow ≥150 MVA for 2 consecutive hours with no equipment overload alarm.
kimi | R9 | A | Unambiguous | applicable transmission path | the 230 kV Main Export Line between Black Start Unit and Grid Substation A
kimi | R9 | V | Verifiable | without assistance from the electrical system | with zero external electrical energy input during the start-up and line energization process
kimi | R10 | U | Understandable | start-up/synchronizing time limits | Hydroelectric generating units shall complete startup within 30 minutes after the dispatcher issues the Black Start command.
kimi | R10 | A | Unambiguous | specific start time limits are negotiated | If the certified Black Start unit uses technology not listed above, its startup completion time shall be documented in the test plan and shall not exceed 4 hours.
kimi | R10 | V | Verifiable | specific start time limits are negotiated | The negotiated startup completion time shall be recorded as a numeric value (minutes) in the test plan and used as the pass/fail criterion.
kimi | R11 | A | Unambiguous | 'technical requirements specified by the CAISO' | 机组须满足CAISO Technical Bulletin 2023-01《Black Start Unit Certification Criteria》第4-7节所列全部技术要求。
kimi | R11 | V | Verifiable | 'must satisfy technical requirements' | 机组应在型式试验中于30分钟内完成黑启动并建立≥5%额定电压，试验报告须由CAISO认可的第三方出具。
kimi | R12 | A | Unambiguous | with or without prior notification | CAISO may conduct performance tests either (a) with no less than 10 business days prior written notice, or (b) without notice when required for emergency reliability assessment.
kimi | R12 | V | Verifiable | from time to time undertake performance tests | CAISO shall execute performance tests at least once per calendar quarter, covering ≥ 80 % of critical-path transactions and achieving ≤ 2 second 95th-percentile response time.
kimi | R13 | A | Unambiguous | conditions on the CAISO Controlled Grid | CAISO shall have the sole authority to initiate Black Start Generating Unit operation upon detection of a total blackout or frequency below 59.0 Hz on the CAISO Controlled Grid.
kimi | R13 | V | Verifiable | determine when the operation...is required | CAISO shall document in the Black Start Event Log the timestamp, measured grid condition values, and decision rationale each time it initiates Black Start Generating Unit operation.
kimi | R14 | U | Understandable | Each of he four points must reside in a different hour of the test. | The four measurement events shall each occur within a distinct 60-minute interval of the 4-hour test run.
kimi | R14 | A | Unambiguous | points | measurement events
kimi | R14 | C | Correctness | he four points | the four measurement events
kimi | R14 | V | Verifiable | reside in a different hour of the test | be timestamped and fall within a unique 60-minute interval (00:00–59:59, 01:00–01:59, 02:00–02:59, 03:00–03:59) of the test run; no two timestamps shall share the same interval
kimi | R15 | A | Unambiguous | “If… Then… The a Black Start unit did not successfully pass…” | If a Black Start unit fails any CAISO Black Start criterion listed in Section 4.2, then…
kimi | R15 | V | Verifiable | “An explanation and a plan to address and correct the deficiency shall be provided…” | The generator owner/operator shall submit to CAISO within 10 business days a written deficiency report and a corrective-action plan that lists each failed criterion, root cause, and scheduled completion date.
kimi | R16 | A | Unambiguous | testing | 每年度执行的内部网络安全渗透测试
kimi | R16 | A | Unambiguous | justification for the periodicity of the testing | 包含风险评估矩阵与测试频率映射表的备忘录
kimi | R16 | C | Correctness | provided to WECC or NERC on request (within 30 days) | 通过 WECC 安全门户上传，且上传完成日期不晚于请求送达后的第 30 个自然日
kimi | R16 | V | Verifiable | justification for the periodicity | 备忘录须说明年度风险等级≥High 的资产比例>5% 时测试频率为年度，否则为每 18 个月
kimi | R17 | U | Understandable | References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203... | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供对应合格报告。
kimi | R17 | A | Unambiguous | References ISO Tariff Section 8.3.3... | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供对应合格报告。
kimi | R17 | V | Verifiable | References ISO Tariff Section 8.3.3... | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供由 CAISO 签署的合格测试报告；验收测试将核查报告存在性及结论为'通过'。
glm5 | R1 | A | Unambiguous | They | The [Target System Name/Generators]
glm5 | R1 | V | Verifiable | adequate voltage and frequency | voltage within [Min V] to [Max V] and frequency within [Min Hz] to [Max Hz]
glm5 | R2 | U | Understandable | Such Test Dispatch Notice | 测试调度通知
glm5 | R2 | A | Unambiguous | shall be marked | 系统应在测试调度通知的【通知类型】字段中显示“Black Start Test Notice”。
glm5 | R2 | V | Verifiable | performed in accordance with the Ancillary Services Requirements Protocol | 系统应依据《CAISO Tariff》中《Ancillary Services Requirements Protocol》第X章节执行黑启动测试流程。
glm5 | R3 | A | Unambiguous | periods of constrained water availability | The CAISO shall not request a Black Start Test for a hydroelectric Unit when the reservoir water level is below [Specific Threshold]% or when a drought emergency is declared by [Authority].
glm5 | R3 | V | Verifiable | periods of constrained water availability | The CAISO shall not request a Black Start Test for a hydroelectric Unit when the reservoir water level is below [Specific Threshold]% or when a drought emergency is declared by [Authority].
glm5 | R4 | A | Unambiguous | Submit any past reports for Black Start tests with the CAISO and WECC. | Submit all Black Start test reports generated within the last 5 years to the CAISO and WECC.
glm5 | R4 | A | Unambiguous | Those Participants who do not currently test their Black Start capability, will be required to test their Black Start capability. | Participants who have not conducted a Black Start test in the preceding 5 years shall conduct a test within 90 days of receiving Black Start generating unit status.
glm5 | R4 | C | Correctness | required by the WECC BCP (if any) and of this testing section. | required by the WECC BCP (if any) and the requirements of this testing section.
glm5 | R4 | V | Verifiable | Demonstrate... that the unit can perform its intended functions as required by the WECC BCP (if any)... | Demonstrate... that the unit meets the specific performance criteria (e.g., start-up time, load acceptance) defined in the WECC BCP and the CAISO Black Start Testing Guide.
glm5 | R5 | A | Unambiguous | dates of the tests | start date and time of each test
glm5 | R5 | A | Unambiguous | an indication of whether the tests met the requirements | a test result status of 'Pass' or 'Fail'
glm5 | R5 | V | Verifiable | duration of the tests | duration of each test in minutes
glm5 | R6 | A | Unambiguous | in accordance with NERC reliability standards | in accordance with NERC PRC-024-2 (or other specific standard ID)
glm5 | R6 | V | Verifiable | emergency voltage limits | voltage limits of [Min Voltage] to [Max Voltage]
glm5 | R6 | V | Verifiable | range of loading from no external load to full external load | loading levels of 0%, 50%, and 100% of rated capacity
glm5 | R7 | C | Correctness | must be equipped | The Black Start unit shall be equipped with governors that are capable of operating in an isochronous mode.
glm5 | R7 | V | Verifiable | capable of operating in an isochronous mode | The Black Start unit shall be equipped with governors capable of isochronous operation, maintaining a steady-state frequency deviation within ±[X] Hz under [Y]% load steps.
glm5 | R8 | A | Unambiguous | Adequate transmission capacity | The transmission capacity shall be no less than [Value] MW.
glm5 | R8 | A | Unambiguous | specified generating stations | generating stations listed in [Reference Document ID]
glm5 | R8 | V | Verifiable | shall be available | The transmission path shall be operational and capable of carrying the required load within [Timeframe] of a request.
glm5 | R9 | A | Unambiguous | applicable transmission path | the transmission path defined in [System_Configuration_Data]
glm5 | R9 | A | Unambiguous | without assistance | while isolated from the external electrical grid
glm5 | R9 | V | Verifiable | must be capable of | shall start and energize
glm5 | R10 | A | Unambiguous | start-up/synchronizing time limits | start-up to synchronizing time limits
glm5 | R10 | A | Unambiguous | Hot, steam-driven turbines | Steam-driven turbines in a Hot state (defined as: turbine metal temperature within 50°C of rated temperature, or downtime less than 48 hours)
glm5 | R10 | V | Verifiable | specific start time limits are negotiated | specific start time limits shall be documented in the Black Start Service Agreement prior to the testing phase
glm5 | R11 | A | Unambiguous | technical requirements specified by the CAISO | All Black Start Generating Units must satisfy the technical requirements specified in 'CAISO Business Practice Manual: Reliability Standards', Version [X], Section [Y].
glm5 | R11 | V | Verifiable | satisfy technical requirements | All Black Start Generating Units must satisfy the technical requirements specified in 'CAISO Business Practice Manual: Reliability Standards', Version [X], Section [Y].
glm5 | R12 | A | Unambiguous | from time to time | The CAISO shall undertake performance tests at least once per calendar year, with or without prior notification.
glm5 | R12 | V | Verifiable | from time to time | The CAISO shall undertake performance tests at least once per calendar year, with or without prior notification.
glm5 | R13 | A | Unambiguous | sole right to determine | The System shall restrict the initiation of Black Start Generating Unit operations to CAISO authorized users.
glm5 | R13 | V | Verifiable | determine when the operation... is required | The System shall provide a control interface for CAISO authorized users to trigger the Black Start Generating Unit operation.
glm5 | R14 | U | Understandable | Each of he four points | Each of the four data points must reside in a different hour of the test.
glm5 | R14 | A | Unambiguous | four points ... different hour | Each of the four data points shall have a timestamp falling within a unique clock hour (e.g., HH:00 to HH:59) during the test execution.
glm5 | R14 | C | Correctness | Each of he | Each of the four points must reside in a different hour of the test.
glm5 | R14 | V | Verifiable | reside in a different hour | The timestamps of the four data points shall fall into four distinct clock hours during the test execution.
glm5 | R15 | U | Understandable | If… Then… The a Black Start unit | If a Black Start unit fails to pass the CAISO Black Start criteria specified in this procedure, the generator owner/operator shall provide an explanation and a corrective plan to the CAISO.
glm5 | R15 | C | Correctness | The a Black Start unit | If a Black Start unit does not successfully pass the CAISO Black Start criteria specified in this procedure, the generator owner/operator shall provide an explanation and a plan to address the deficiency to the CAISO.
glm5 | R15 | V | Verifiable | An explanation and a plan | If a Black Start unit fails the CAISO Black Start criteria, the generator owner/operator shall submit a written explanation and a corrective action plan to the CAISO.
glm5 | R16 | A | Unambiguous | on request (within 30 days) | within 30 days of receiving a request
glm5 | R16 | V | Verifiable | justification for the periodicity of the testing | a documented justification for the periodicity of the testing
glm5 | R17 | U | Understandable | References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203... | 系统应遵守以下标准与规程： 1. ISO Tariff Section 8.3.3 Certification and Testing Requirements； 2. CAISO Operating Procedure G-203 Reliability Must Run Unit Commitment and Dispatch； 3. CAISO Operating Procedure G-213 Generator Certification Testing； 4. CAISO Operating Procedure G-213H Black Start Test Report Form； 5. CAISO Operating Procedure G-213I Black Start Process Flowchart； 6. NERC Reliability Standard EOP-005 System Restoration Plans； 7. EOP-009 Documentation of Blackstart Generating Unit Test Results。
glm5 | R17 | A | Unambiguous | References | 系统应遵守以下标准与规程...
glm5 | R17 | V | Verifiable | References ISO Tariff Section 8.3.3... | 系统应遵守以下标准与规程...（验证方法：检查系统设计文档或功能实现是否符合所列标准的具体条款）。

## issue_scores_r0
item | type | S_issue | dimension
R6 | V | 0.86667 | Verifiable
R17 | V | 0.86667 | Verifiable
R17 | A | 0.8 | Unambiguous
R12 | V | 0.8 | Verifiable
R9 | A | 0.8 | Unambiguous
R6 | A | 0.8 | Unambiguous
R2 | V | 0.8 | Verifiable
R2 | A | 0.8 | Unambiguous
R17 | U | 0.8 | Understandable
R13 | V | 0.8 | Verifiable
R13 | A | 0.8 | Unambiguous
R9 | V | 0.8 | Verifiable
R11 | V | 0.8 | Verifiable
R12 | A | 0.8 | Unambiguous
R11 | A | 0.8 | Unambiguous
R1 | A | 0.7 | Unambiguous
R14 | A | 0.7 | Unambiguous
R1 | V | 0.7 | Verifiable
R14 | U | 0.7 | Understandable
R14 | V | 0.7 | Verifiable
R8 | V | 0.7 | Verifiable
R8 | A | 0.7 | Unambiguous
R16 | A | 0.7 | Unambiguous
R16 | V | 0.7 | Verifiable
R10 | A | 0.63333 | Unambiguous
R4 | A | 0.63333 | Unambiguous
R3 | V | 0.63333 | Verifiable
R10 | V | 0.63333 | Verifiable
R3 | A | 0.63333 | Unambiguous
R15 | V | 0.63333 | Verifiable
R5 | A | 0.56667 | Unambiguous
R5 | V | 0.56667 | Verifiable
R15 | U | 0.53333 | Understandable
R2 | U | 0.53333 | Understandable
R14 | C | 0.53333 | Correctness
R15 | A | 0.53333 | Unambiguous
R4 | V | 0.43333 | Verifiable
R7 | V | 0.37778 | Verifiable
R10 | U | 0.36667 | Understandable
R7 | A | 0.36667 | Unambiguous
R15 | C | 0.26667 | Correctness
R7 | C | 0.26667 | Correctness
R11 | U | 0.26667 | Understandable
R1 | U | 0.26667 | Understandable
R4 | U | 0.26667 | Understandable
R16 | U | 0.26667 | Understandable
R12 | U | 0.26667 | Understandable
R6 | U | 0.16667 | Understandable
R4 | C | 0.16667 | Correctness
R7 | U | 0.16667 | Understandable
R3 | U | 0.16667 | Understandable
R8 | U | 0.16667 | Understandable
R13 | U | 0.16667 | Understandable
R9 | U | 0.16667 | Understandable
R16 | C | 0.1 | Correctness

## issue_scores_r1
item | type | S_issue | dimension
R17 | V | 0.86667 | Verifiable
R6 | V | 0.86667 | Verifiable
R17 | A | 0.8 | Unambiguous
R2 | V | 0.8 | Verifiable
R17 | U | 0.8 | Understandable
R2 | A | 0.8 | Unambiguous
R13 | V | 0.8 | Verifiable
R13 | A | 0.8 | Unambiguous
R12 | V | 0.8 | Verifiable
R11 | V | 0.8 | Verifiable
R6 | A | 0.8 | Unambiguous
R11 | A | 0.8 | Unambiguous
R9 | A | 0.8 | Unambiguous
R16 | A | 0.7 | Unambiguous
R8 | A | 0.7 | Unambiguous
R8 | V | 0.7 | Verifiable
R16 | V | 0.7 | Verifiable
R1 | A | 0.7 | Unambiguous
R1 | V | 0.7 | Verifiable
R14 | V | 0.7 | Verifiable
R14 | U | 0.7 | Understandable
R14 | A | 0.7 | Unambiguous
R4 | A | 0.63333 | Unambiguous
R3 | A | 0.63333 | Unambiguous
R15 | V | 0.63333 | Verifiable
R10 | A | 0.63333 | Unambiguous
R10 | V | 0.63333 | Verifiable
R3 | V | 0.63333 | Verifiable
R5 | V | 0.56667 | Verifiable
R5 | A | 0.56667 | Unambiguous
R15 | U | 0.53333 | Understandable
R9 | V | 0.53333 | Verifiable
R2 | U | 0.53333 | Understandable
R15 | A | 0.53333 | Unambiguous
R14 | C | 0.53333 | Correctness
R12 | A | 0.53333 | Unambiguous
R4 | V | 0.43333 | Verifiable
R7 | V | 0.37778 | Verifiable
R7 | A | 0.36667 | Unambiguous
R10 | U | 0.36667 | Understandable
R16 | U | 0.26667 | Understandable
R7 | C | 0.26667 | Correctness
R15 | C | 0.26667 | Correctness
R11 | U | 0.26667 | Understandable
R1 | U | 0.26667 | Understandable
R4 | U | 0.26667 | Understandable
R7 | U | 0.16667 | Understandable
R8 | U | 0.16667 | Understandable
R4 | C | 0.16667 | Correctness
R3 | U | 0.16667 | Understandable
R16 | C | 0.1 | Correctness

## team_scores_r0
item | dim | team_score
R1 | A | 2
R1 | C | 3
R1 | U | 2.5789
R1 | V | 1.619
R10 | A | 2.1579
R10 | C | 3
R10 | U | 3
R10 | V | 1.7368
R11 | A | 2
R11 | C | 2.5455
R11 | U | 3
R11 | V | 1.3333
R12 | A | 2
R12 | C | 3
R12 | U | 3
R12 | V | 1.3333
R13 | A | 2
R13 | C | 3.6667
R13 | U | 2.6667
R13 | V | 1.6667
R14 | A | 2
R14 | C | 2.619
R14 | U | 2.619
R14 | V | 1.619
R15 | A | 2.2381
R15 | C | 2.5
R15 | U | 2.2381
R15 | V | 1.7368
R16 | A | 2.2381
R16 | C | 3.1111
R16 | U | 3
R16 | V | 1.8571
R17 | A | 2
R17 | C | 3
R17 | U | 2
R17 | V | 1.3077
R2 | A | 2
R2 | C | 3.4444
R2 | U | 2.619
R2 | V | 1.6667
R3 | A | 2
R3 | C | 3
R3 | U | 2.6667
R3 | V | 1.5789
R4 | A | 2.1579
R4 | C | 3
R4 | U | 2.5789
R4 | V | 2.6154
R5 | A | 2
R5 | C | 3.75
R5 | U | 3.7222
R5 | V | 2
R6 | A | 2
R6 | C | 3
R6 | U | 3.1667
R6 | V | 1.6923
R7 | A | 2.8125
R7 | C | 3
R7 | U | 3.1875
R7 | V | 2
R8 | A | 2
R8 | C | 3
R8 | U | 2.6667
R8 | V | 1.619
R9 | A | 2
R9 | C | 3.1429
R9 | U | 3.1667
R9 | V | 1.6667

## team_scores_r1
item | dim | team_score
R1 | A | 2
R1 | C | 3
R1 | U | 2.5789
R1 | V | 1.619
R10 | A | 2.1579
R10 | C | 3
R10 | U | 3
R10 | V | 1.7368
R11 | A | 2
R11 | C | 2.5455
R11 | U | 3
R11 | V | 1.3333
R12 | A | 2.3333
R12 | C | 3
R12 | U | 3.381
R12 | V | 1.3333
R13 | A | 1.6667
R13 | C | 3.4706
R13 | U | 3
R13 | V | 1.6667
R14 | A | 2
R14 | C | 2.619
R14 | U | 2.619
R14 | V | 1.619
R15 | A | 2.2381
R15 | C | 2.5
R15 | U | 2.2381
R15 | V | 1.7368
R16 | A | 2.2381
R16 | C | 3.1111
R16 | U | 3
R16 | V | 1.8571
R17 | A | 1.6667
R17 | C | 3
R17 | U | 1.6667
R17 | V | 1.3077
R2 | A | 1.6667
R2 | C | 3.3333
R2 | U | 2.619
R2 | V | 1.6667
R3 | A | 2
R3 | C | 3
R3 | U | 2.6667
R3 | V | 1.5789
R4 | A | 2.1579
R4 | C | 3
R4 | U | 2.5789
R4 | V | 2.6154
R5 | A | 2
R5 | C | 3.75
R5 | U | 3.7222
R5 | V | 2
R6 | A | 1.6667
R6 | C | 3
R6 | U | 3.381
R6 | V | 1.6923
R7 | A | 2.8125
R7 | C | 3
R7 | U | 3.1875
R7 | V | 2
R8 | A | 2
R8 | C | 3
R8 | U | 2.6667
R8 | V | 1.619
R9 | A | 1.6667
R9 | C | 3.0833
R9 | U | 3.381
R9 | V | 2.3333

## final_problems
item | type | S_issue | dimension | text | best_evidence | best_rewrite | top_supporters
R17 | V | 0.86667 | Verifiable | References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203, Reliability Must Run Unit Commitment and Dispatch CAISO Operating Procedure G-213 Generator Certification Testing CAISO Operating Procedure G-213H Black Start Test Report Form CAISO Operating Procedure G-213I Black Start Process Flowchart NERC Reliability Standard EOP-005 System Restoration Plans EOP-009 Documentation of Blackstart Generating Unit Test Results | References ISO Tariff Section 8.3.3... | 系统应遵守以下标准与规程...（验证方法：检查系统设计文档或功能实现是否符合所列标准的具体条款）。 | [{"rater": "glm5", "influence": 0.3333333333333333}, {"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}]
R6 | V | 0.86667 | Verifiable | The Black Start unit must have the ability to maintain voltage within emergency voltage limits over a range of loading from no external load to full external load in accordance with NERC reliability standards. | emergency voltage limits | voltage limits of [Min Voltage] to [Max Voltage] | [{"rater": "glm5", "influence": 0.3333333333333333}, {"rater": "glm5", "influence": 0.3333333333333333}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.26666666666666666}]
R13 | A | 0.8 | Unambiguous | The CAISO shall have the sole right to determine when the operation of Black Start Generating Unit is required to respond to conditions on the CAISO Controlled Grid. | conditions on the CAISO Controlled Grid | CAISO shall have the sole authority to initiate Black Start Generating Unit operation upon detection of a total blackout or frequency below 59.0 Hz on the CAISO Controlled Grid. | [{"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.26666666666666666}]
R9 | A | 0.8 | Unambiguous | The Black Start unit must be capable of starting and energizing the applicable transmission path without assistance from the electrical system. | applicable transmission path | the 230 kV Main Export Line between Black Start Unit and Grid Substation A | [{"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}]
R11 | A | 0.8 | Unambiguous | All Black Start Generating Units must satisfy technical requirements specified by the CAISO. | 'technical requirements specified by the CAISO' | 机组须满足CAISO Technical Bulletin 2023-01《Black Start Unit Certification Criteria》第4-7节所列全部技术要求。 | [{"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}]
R6 | A | 0.8 | Unambiguous | The Black Start unit must have the ability to maintain voltage within emergency voltage limits over a range of loading from no external load to full external load in accordance with NERC reliability standards. | in accordance with NERC reliability standards | in accordance with NERC PRC-024-2 (or other specific standard ID) | [{"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.26666666666666666}]
R11 | V | 0.8 | Verifiable | All Black Start Generating Units must satisfy technical requirements specified by the CAISO. | 'must satisfy technical requirements' | 机组应在型式试验中于30分钟内完成黑启动并建立≥5%额定电压，试验报告须由CAISO认可的第三方出具。 | [{"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}]
R12 | V | 0.8 | Verifiable | The CAISO shall from time to time undertake performance tests, with or without prior notification. | from time to time undertake performance tests | CAISO shall execute performance tests at least once per calendar quarter, covering ≥ 80 % of critical-path transactions and achieving ≤ 2 second 95th-percentile response time. | [{"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}]
R13 | V | 0.8 | Verifiable | The CAISO shall have the sole right to determine when the operation of Black Start Generating Unit is required to respond to conditions on the CAISO Controlled Grid. | determine when the operation...is required | CAISO shall document in the Black Start Event Log the timestamp, measured grid condition values, and decision rationale each time it initiates Black Start Generating Unit operation. | [{"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}]
R2 | A | 0.8 | Unambiguous | Such Test Dispatch Notice shall be marked “Black Start Test Notice.” The Black Start Test shall be performed in accordance with the Ancillary Services Requirements Protocol in the CAISO Tariff. | shall be marked | 系统应在测试调度通知的【通知类型】字段中显示“Black Start Test Notice”。 | [{"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}]
R17 | U | 0.8 | Understandable | References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203, Reliability Must Run Unit Commitment and Dispatch CAISO Operating Procedure G-213 Generator Certification Testing CAISO Operating Procedure G-213H Black Start Test Report Form CAISO Operating Procedure G-213I Black Start Process Flowchart NERC Reliability Standard EOP-005 System Restoration Plans EOP-009 Documentation of Blackstart Generating Unit Test Results | References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203... | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供对应合格报告。 | [{"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}]
R2 | V | 0.8 | Verifiable | Such Test Dispatch Notice shall be marked “Black Start Test Notice.” The Black Start Test shall be performed in accordance with the Ancillary Services Requirements Protocol in the CAISO Tariff. | performed in accordance with the Ancillary Services Requirements Protocol | 系统应依据《CAISO Tariff》中《Ancillary Services Requirements Protocol》第X章节执行黑启动测试流程。 | [{"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.26666666666666666}]
R17 | A | 0.8 | Unambiguous | References ISO Tariff Section 8.3.3 Certification and Testing Requirements CAISO Operating Procedure G-203, Reliability Must Run Unit Commitment and Dispatch CAISO Operating Procedure G-213 Generator Certification Testing CAISO Operating Procedure G-213H Black Start Test Report Form CAISO Operating Procedure G-213I Black Start Process Flowchart NERC Reliability Standard EOP-005 System Restoration Plans EOP-009 Documentation of Blackstart Generating Unit Test Results | References ISO Tariff Section 8.3.3... | 系统须符合 CAISO Operating Procedure G-203 §8.3.3 的认证与测试要求，并在交付时提供对应合格报告。 | [{"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}]
R1 | V | 0.7 | Verifiable | They must be able to self-start without any source of off-site electric power and maintain adequate voltage and frequency while energizing isolated transmission facilities and auxiliary loads of other generators. | adequate voltage and frequency | voltage within [Min V] to [Max V] and frequency within [Min Hz] to [Max Hz] | [{"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.16666666666666666}]
R14 | A | 0.7 | Unambiguous | Each of he four points must reside in a different hour of the test. | points | measurement events | [{"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.16666666666666666}]
R14 | U | 0.7 | Understandable | Each of he four points must reside in a different hour of the test. | Each of he four points | Each of the four data points must reside in a different hour of the test. | [{"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.16666666666666666}]
R14 | V | 0.7 | Verifiable | Each of he four points must reside in a different hour of the test. | reside in a different hour of the test | be timestamped and fall within a unique 60-minute interval (00:00–59:59, 01:00–01:59, 02:00–02:59, 03:00–03:59) of the test run; no two timestamps shall share the same interval | [{"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.16666666666666666}]
R8 | A | 0.7 | Unambiguous | Adequate transmission capacity shall be available to connect the Black Start facility to the source providing station services to other specified generating stations. | specified generating stations | generating stations listed in [Reference Document ID] | [{"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.16666666666666666}, {"rater": "kimi", "influence": 0.16666666666666666}]
R1 | A | 0.7 | Unambiguous | They must be able to self-start without any source of off-site electric power and maintain adequate voltage and frequency while energizing isolated transmission facilities and auxiliary loads of other generators. | They | The [Target System Name/Generators] | [{"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.16666666666666666}]
R16 | V | 0.7 | Verifiable | The results of the testing and the justification for the periodicity of the testing shall be provided to WECC or NERC on request (within 30 days). | justification for the periodicity | 备忘录须说明年度风险等级≥High 的资产比例>5% 时测试频率为年度，否则为每 18 个月 | [{"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.16666666666666666}]
R8 | V | 0.7 | Verifiable | Adequate transmission capacity shall be available to connect the Black Start facility to the source providing station services to other specified generating stations. | shall be available | The transmission path shall be operational and capable of carrying the required load within [Timeframe] of a request. | [{"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.16666666666666666}]
R16 | A | 0.7 | Unambiguous | The results of the testing and the justification for the periodicity of the testing shall be provided to WECC or NERC on request (within 30 days). | justification for the periodicity of the testing | 包含风险评估矩阵与测试频率映射表的备忘录 | [{"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.16666666666666666}]
R4 | A | 0.63333 | Unambiguous | The owner or operator of any Voluntary Black Start unit that desires a Black Start generating unit status with the CAISO Balancing Authority shall: • Demonstrate at least every five years, through simulation or testing, that the unit can perform its intended functions as required by the WECC BCP (if any) and of this testing section. • Submit documentation of the test results and analysis to the CAISO, WECC, or NERC upon any request. • Submit any past reports for Black Start tests with the CAISO and WECC. o Those Participants who do not currently test their Black Start capability, will be required to test their Black Start capability. • Within 24 hours of conducting a Black Start test, all Participants will notify the CAISO RT Dispatcher by phone indicating the success or failure of the test. • Within 14 days of performing a Black Start test, all Participants will file a letter with the CAISO regarding the success or failure of the test. | Those Participants who do not currently test their Black Start capability, will be required to test their Black Start capability. | Participants who have not conducted a Black Start test in the preceding 5 years shall conduct a test within 90 days of receiving Black Start generating unit status. | [{"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.09999999999999999}]
R3 | A | 0.63333 | Unambiguous | The CAISO shall not request a Black Start Test for a hydroelectric Unit during periods of constrained water availability. | periods of constrained water availability | The CAISO shall not request a Black Start Test for a hydroelectric Unit when the reservoir water level is below [Specific Threshold]% or when a drought emergency is declared by [Authority]. | [{"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.09999999999999999}]
R15 | V | 0.63333 | Verifiable | If… Then… The a Black Start unit did not successfully pass the CAISO Black Start criteria specified in this procedure, An explanation and a plan to address and correct the deficiency shall be provided to the CAISO by the generator owner/operator. | “An explanation and a plan to address and correct the deficiency shall be provided…” | The generator owner/operator shall submit to CAISO within 10 business days a written deficiency report and a corrective-action plan that lists each failed criterion, root cause, and scheduled completion date. | [{"rater": "kimi", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.09999999999999999}]
R10 | A | 0.63333 | Unambiguous | The following start-up/synchronizing time limits shall apply to the Black Start testing units: • Hydroelectric generating units or combustion gas turbines - within 30 minutes of the initiation of the Black Start process, • Industrial gas turbines - within 60 minutes of the initiation of the Black Start process, • Hot, steam-driven turbines, within 2.5 hours of the initiation of the Black Start process. • If the certified Black Start facility is in another reliability coordinator area or is comprised of an unspecified technology then specific start time limits are negotiated. | Hot, steam-driven turbines | Steam-driven turbines in a Hot state (defined as: turbine metal temperature within 50°C of rated temperature, or downtime less than 48 hours) | [{"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.09999999999999999}]
R10 | V | 0.63333 | Verifiable | The following start-up/synchronizing time limits shall apply to the Black Start testing units: • Hydroelectric generating units or combustion gas turbines - within 30 minutes of the initiation of the Black Start process, • Industrial gas turbines - within 60 minutes of the initiation of the Black Start process, • Hot, steam-driven turbines, within 2.5 hours of the initiation of the Black Start process. • If the certified Black Start facility is in another reliability coordinator area or is comprised of an unspecified technology then specific start time limits are negotiated. | specific start time limits are negotiated | specific start time limits shall be documented in the Black Start Service Agreement prior to the testing phase | [{"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.09999999999999999}]
R3 | V | 0.63333 | Verifiable | The CAISO shall not request a Black Start Test for a hydroelectric Unit during periods of constrained water availability. | periods of constrained water availability | The CAISO shall not request a Black Start Test for a hydroelectric Unit when the reservoir water level is below [Specific Threshold]% or when a drought emergency is declared by [Authority]. | [{"rater": "glm5", "influence": 0.26666666666666666}, {"rater": "qwen", "influence": 0.26666666666666666}, {"rater": "kimi", "influence": 0.09999999999999999}]